## 000-P-PQP-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | 300060 | Line item for Preservation performed after all functioning testing is completed needs adding.
2 | Call-out | 2 | CK Samy | indicate page no. and separate sheet for each equipments
3 | Text Box | 3 | CK Samy | A. Include following missing electrical equipments and components 1. Bus ducts 2. control and relay panels 3. Local control station/welding receptacles 4. Earthing system 5. Lightning protection 6. communication equipments 7. Power capacitors 8. Cable splices and termination
4 | Text Box | 3 | CK Samy | B. Indicate reference documents/codes/standards/specification
5 | Text Box | 3 | Jongman.Kim | General comments: 1. Precomm/Commissioning forms for the following shall be prepared and submitted; - EMCS - NER 2. Function test for Emergency Diesel Generator shall be added. 3. With regard to the switchgear, the following test shall be added: - check list for all outgoing feeders - detail interlock/interface function test - 1ry or 2ry injection test for all protection relays 4. It is recommended to separate the aircraft warning system from the power/lighting distribution board.
6 | Cloud+ | 4 | CK Samy | separate sheets for oil type HV/LV and dry type transformer
7 | Call-out | 9 | CK Samy | separate checks/tests for be indicated for High voltage, low voltage, synchronous motors