## 000-P-SYM-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mohamed Aldoseri | ---------------
2 | Text Box | 1 | Mohamed Aldoseri | Symbol
3 | Callout | 1 | Jongman.Kim | To be corrected to "VOLTMETER"
4 | Pen | 1 | Jongman.Kim | . . .
5 | Call-out | 1 | MAK | 1
6 | Call-out | 1 | Mohamed Aldoseri | BK=BLACK
7 | Call-out | 1 | Mohamed Aldoseri | BUCHHOLZ ALARM/TRIP
8 | Callout | 1 | Sankara | Call as Small Power Panel
9 | Text Box | 1 | Jongman.Kim | Contractor shall check and correct the abbreviation and description
10 | Call-out | 1 | Mohamed Aldoseri | DIAGRAMS
11 | Text Box | 1 | Jongman.Kim | EMERGENCY DIESEL GENERATOR
12 | Text Box | 1 | Mohamed Aldoseri | FM-Feeder Manager
13 | Text Box | 1 | Mohamed Aldoseri | Future equipment/spare
14 | Text Box | 1 | Mohamed Aldoseri | Future equipment/spare Anti condinsation heater Inverter Rectifier Distribution Panel
15 | Text Box | 1 | Mohamed Aldoseri | Graphical symbols for Single Line Diagrams and Schematic Diagrams must be as described in BMPS-P3, P26. Ammend necessary changes on all SLD's and consider it before issuing Schematic diagrams.
16 | Text Box | 1 | Mohamed Aldoseri | High Voltage Low Voltage Local control station Short circuit KVA meter Air Circuit Breaker Direct On Line Emergency Shutdown
17 | Call-out | 1 | CK Samy | Include abbreviations for the following Closing coil Trip coil Oil temperature indicator/Alarm Winding temp Alarm/Trip Buchholz Alarm/ trip Oil Natural Air Natural Oil Natural Air forced Motor Control centre Power control centre
18 | Call-out | 1 | CK Samy | Include following relays 11 -Multifunction relay 30 -Annunciator relay 60 - Voltage /current balance relay 72 -DC circuit breaker 74 - Supervision relay
19 | Call-out | 1 | CK Samy | Include following symbols Timer contactor coil NO/NC contacts Thermal overload relay MCB Terminal (Motor/DCS/Field/switchgear etc.,)
20 | Text Box | 1 | Mohamed Aldoseri | increase line thickness
21 | Call-out | 1 | CK Samy | Indicate separate for SPBD and NSPBD
22 | Call-out | 1 | CK Samy | Indicate star connected capacitor bank also (for MV/HV)
23 | Text Box | 1 | Mohamed Aldoseri | Indicating Lamp Photocell Emergency push botton
24 | Call-out | 1 | CK Samy | Line switch
25 | Call-out | 1 | MAK | NTS
26 | Text Box | 1 | Khaled.Delaim | Please revise and follow the FEED descriptions and symbology for single line diagrams
27 | Cloud+ | 1 | Khaled.Delaim | please revise the description
28 | Cloud+ | 1 | Khaled.Delaim | please revise the description
29 | Call-out | 1 | Mohamed Aldoseri | Provide a circle around the protection symbols
30 | Call-out | 1 | Mohamed Aldoseri | Reference the grounding and lightning system general philosophy drawing (000-P-PHD-50001-001)
31 | Call-out | 1 | Mohamed Aldoseri | re-write description to: RESTRICTED EARTH FAULT RELAY
32 | Call-out | 1 | CK Samy | Symbol shall be corrected. Looks similar to voltage transformer
33 | Callout | 1 | Jongman.Kim | To be corrected to "11kV"
34 | Text Box | 1 | Jongman.Kim | To be filled-up
35 | Text Box | 1 | Mahdi Ali | TTSJV shall utilize SLD and Schematics symbols provided in the SPEL seed file. any additional symbols will have to be reviewed and approved individually by Bapco. TTSJV to highlight additional symbols that are not part of the SPEL seed file.
36 | Call-out | 1 | MAK | Use first and second lines of the Title
37 | Text Box | 1 | MAK | Use the latest border that is part of the Homogenization Procedure. TR shall coordinate with JV Directorate.