## 000-Q-MST-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | TSP shall be used for TECHNICAL SPECIFICAITONS
2 | Callout | 6 | Joon Cho | <Add> Gravel paving work
3 | Callout | 6 | Joon Cho | <Add> Disposal work
4 | Callout | 6 | Bernard.Grace | supply, installation and making good
5 | Callout | 6 | Joon Cho | <Add> Sewer & Drainage work
6 | Callout | 6 | Joon Cho | <Clarify> SOW for Fence & Gate work included or not ?
7 | Callout | 6 | Bernard.Grace | finishing
8 | Callout | 7 | Mahdi Ali | INCORRECT UNIT ABBREVIATIONS
9 | Text Box | 9 | Chandrahasan D | Include Technical specification for marine works
10 | Callout | 9 | Joon Cho | <Add> BMPS-SD-M-10281, BMPS-S-69015, 69016, 50805, 10192, 200531, 221537, 31743
11 | Text Box | 9 | Chandrahasan D | Include document title for each listed document number
12 | Callout | 9 | Joon Cho | <Add> BMPS-SD-S-10207, 78986, 50813
13 | Text Box | 9 | Chandrahasan D | Include document title for each listed document number
14 | Callout | 9 | Joon Cho | 10280
15 | Text Box | 9 | Antony.Bentley | Add note to say if there are any discrepancies between this Specification & the BMPS's then the BMPS's take precedence
16 | Callout | 9 | Joon Cho | <Add> BMPS-Q-141752 for Anchor Bolts Standard
17 | Callout | 9 | Mahdi Ali | NORMALLY BASIS OF DESIGNS HAS 'BOD' AS DOCUMENT TYPE. THIS IS USING TSP WHICH IS FOR SPECIFICATIONS
18 | Callout | 10 | Salman Almajed | Align the text.
19 | Callout | 11 | Joon Cho | <Add> BMPS-M6 for Fireproofing
20 | Text Box | 13 | Chandrahasan D | Include year / edition for international standards (wherever missing), to be clear and to be consistent.
21 | Callout | 16 | Chandrahasan D | OR Bahrain National Survey datum as applicable.
22 | Cloud+ | 16 | Salman Almajed | Bahrain
23 | Callout | 16 | Chandrahasan D | OR UTM as applicable
24 | Callout | 18 | Mahdi Ali | THE LIST OF UNIT DESCRIPTIONS AND ABBREVIATIONS ARE NOT THE LATEST.
25 | Text Box | 18 | Antony.Bentley | Explain colour coding or remove
26 | Callout | 20 | Chandrahasan D | In general ,excavation in brown field areas to be carried out by manual method using hand tools.
27 | Callout | 21 | Mahdi Ali | MATERIAL CLASS FOR PLOT PLANS IS 'A' AND NOT 'L'
28 | Callout | 21 | Danut.Dragan | "supporting" should be added
29 | Callout | 21 | Mahdi Ali | DO NOT USE FEED NUMBERS
30 | Callout | 21 | Danut.Dragan | "Building Instrument / Electric Cable Entrance - MCT (Cable Transits) as per relevant Specifications" new bulled should be added
31 | Callout | 21 | Mahdi Ali | MATERIAL CLASS IS MISSING
32 | Callout | 23 | Mahdi Ali | INCORRECT MATERIAL CLASS. CHANGE TO 'A'
33 | Callout | 23 | Mahdi Ali | DO NOT USE FEED NUMBERS. USE BAPCO NUMBERS
34 | Callout | 23 | Mahdi Ali | UNIT 000 DOES NOT EXIST. THIS WAS REPLACE BY THE INTERCONNECTING AREAS WITH DEDICATED UNIT NUMBERS
35 | Text Box | 23 | Mahdi Ali | MAKE SURE THAT FOR REVAMP UNITS TO CONTACT BAPCO FOR THE PLOT PLAN DRAWINGS. DO NOT USE FEED PLOT PLANS
36 | Callout | 23 | Mahdi Ali | MATERIAL CLASS IS MISSING IN THE DRAWING NUMBER
37 | Callout | 24 | Mahdi Ali | USE BAPCO NUMBERS
38 | Callout | 24 | Mahdi Ali | CHANGE TO 096-S-SUR-00002-001
39 | Callout | 26 | Chandrahasan D | Since, the treatment will be done by others, the treated soil may not be available for BMP use as backfill material. Review and modify this part of the sentence.
40 | Callout | 26 | Chandrahasan D | and the location of these stockpiles shall be agreed with operational personnel.
41 | Callout | 26 | Chandrahasan D | use
42 | Callout | 27 | Chandrahasan D | use
43 | Callout | 27 | Salman Almajed | as specified in the drawings or method statement
44 | Callout | 27 | Chandrahasan D | Since, the treatment will be done by others, the treated soil may not be available for BMP use as backfill material. Review and modify this part of the sentence.
45 | Callout | 28 | Salman Almajed | as specified in the drawings or method statement
46 | Callout | 28 | Salman Almajed | as specified in the drawings or method statement
47 | Callout | 29 | Danut.Dragan | "and Isntrument" should be added
48 | Callout | 30 | Joon Cho | <Add & insert> in accordance with section 5.3 BMPS-Q2
49 | Callout | 30 | Joon Cho | Shall
50 | Callout | 30 | Chandrahasan D | Revise to : unless otherwise specified by the supplier.
51 | Callout | 31 | Salman Almajed | Civil Standard Paving and Details BMPS-S-50805
52 | Callout | 32 | Joon Cho | SS ?, Need to clarify
53 | Callout | 32 | Salman Almajed | Add the following missing drawings: 2520-S000-DW-1442-01-01/02/03/04/05 2520-U341-DW-1442-01-01 2520-U372-DW-1442-01-01 2520-U381-DW-1442-01-01 2520-C018-DW-1442-01-01/02 2520-C019-DW-1442-01-01 2520-C021-DW-1442-01-01 2520-F000-DW-1442-01-01/02/03/04 2520-H000-DW-1442-01-01/02 2520-R000-DW-1442-01-01
54 | Callout | 32 | Salman Almajed | as
55 | Callout | 32 | Mahdi Ali | USE BAPCO NUMBERS
56 | Callout | 34 | Joon Cho | <Recommend> Replace with E&I requirements in BMPS, if any or UG section for E&I cable in FEED
57 | Cloud+ | 34 | Salman Almajed | <Replace> Concrete tiles
58 | Callout | 35 | Joon Cho | Civil Standard for Road cross sections and details BMPS-S-69015 & Road Intersections within Refinery Area BMPS-SD-S-10192
59 | Cloud+ | 36 | Salman Almajed | 75 mm thick un-reinforced concrete (and 60 mm thick precast concrete) is not acceptable for walkways. Contractor to use light duty paving (thickness of 100 mm) in accordance with Civil Standard Paving and Details drawing BMPS-S-50805.
60 | Callout | 37 | Danut.Dragan | "..., handholes, ..." should be added where / if split FO or other cable T routing hand holes are used.
61 | Callout | 39 | Chandrahasan D | vacuum tankers
62 | Callout | 44 | Salman Almajed | Maximum thickness of fill layer is 200 mm, according to BMPS-S2
63 | Callout | 48 | Joon Cho | <Add> Epoxy-coated reinforcing steel bar shall also be used for all concrete structures at Unit 005 C3/C4 LPG storage bullets and all concrete structures exposed to marine environment whether close to sea or at splash zone or subsea.
64 | Callout | 48 | Joon Cho | <Add> and ASTM A884 Wire and Welded Wire Fabric
65 | Text Box | 49 | Chandrahasan D | <Add> specification of binding wire for coated and non-coated reinforcement
66 | Callout | 49 | Joon Cho | <Add> Chapter 7. TYPE OF PORTLAND CEMENT in BMPS-M2 shall be added.
67 | Callout | 49 | Joon Cho | <Add> Proper drainage and protection from mud, soil and water shall be provided to minimize corrosion.
68 | Callout | 49 | Chandrahasan D | OR as specified in the drawings
69 | Callout | 49 | Joon Cho | <Add> Storage & Handling requirements for Epoxy-coated steel reinforcement in section 15.4.2 BMPS-M2 shall be added.
70 | Callout | 52 | Joon Cho | pH value between 6 and 8 as per BMPS-M2
71 | Callout | 52 | Joon Cho | <Add> Requirements in section 8.3.3 Aggregates for Sulphur Pits in BMPS-M2 shall be added
72 | Callout | 53 | Salman Almajed | 0.6-0.9
73 | Callout | 53 | Salman Almajed | Repeated points
74 | Callout | 54 | Salman Almajed | <Add> by SITE MANAGEMENT
75 | Callout | 55 | Chandrahasan D | Anchor bolt type as specified in the drawing
76 | Callout | 56 | Salman Almajed | Standard Deviation shall be less than 3.5 MPa, as per section 13.1.4 of BMPS-M2.
77 | Callout | 56 | Joon Cho | section 9.3 of BMPS-M2
78 | Callout | 57 | Joon Cho | Table shall be developed as per section 9.7 Slump Table 11 of BMPS-M2
79 | Callout | 58 | Salman Almajed | According to sec. 13.1.5 of BMPS-M2, tests shall be carried out at 7 days to establish a relationship between the 7 day and 28 day strengths.
80 | Callout | 62 | Salman Almajed | <Add> Concrete spacers shall have the same inherent properties as the parent material, but with the exception that the maximum aggregate size shall be appropriate for the thickness of cover to the reinforcement. (Sec. 15.6.4 of BMPS-M2)
81 | Callout | 62 | Joon Cho | 1.5 mm diameter as per section 15.6.1 of BMPS-M2
82 | Text Box | 63 | Salman Almajed | and
83 | Cloud+ | 63 | Salman Almajed | Contractor to verify and prove the requirement of washing the reinforcement, as per relevant code or standard.
84 | Callout | 63 | Joon Cho | +10/-0 mm as per section 24.1.2 of BMPS-M2
85 | Text Box | 63 | Salman Almajed | trichloroethylene
87 | Callout | 68 | Salman Almajed | Temperature of 32 degrees C is exceeding the limit of BMPS requirement (30 degrees C).
88 | Callout | 68 | Joon Cho | <Add> For Sulphur pits, temperature of concrete at time of placement shall not exceed 27 degree C as per section 11.4.1 of BMPS-M2
89 | Callout | 69 | Chandrahasan D | <Add> underwater concreting requirements (tremie pipe etc ), if not covered elsewhere.
90 | Callout | 69 | Salman Almajed | This paragraph was repeated in the previous page.
91 | Callout | 70 | Salman Almajed | <Add> The surface shall be roughened by pressure jetting with air and water or wire brushing. (BMPS-M2, sec. 17.5.2)
92 | Callout | 73 | Joon Cho | <Add> Water curing shall be continuous until the compressive strength has reached 70% of the specified strength and for 14 days minimum.
93 | Callout | 73 | Chandrahasan D | Applying of bonding agent
94 | Callout | 73 | Salman Almajed | Contractor to develop this section and add the missing details as mentioned in sec. 18 of BMPS-M2.
95 | Callout | 73 | Salman Almajed | <Add> Roughening the concrete surface
96 | Callout | 74 | Joon Cho | shall
99 | Callout | 74 | Joon Cho | section 5.3
100 | Callout | 74 | Salman Almajed | <Add> for base plates up to 0.9 m, with an additional 25 mm of grout for each additional 0.9 m in width.(BMPS-Q2 sec. 8.1.2)
102 | Callout | 75 | Joon Cho | at least 14 days as per section 7.1.1 of BMPS-Q2
103 | Callout | 82 | Chandrahasan D | This section needs to be developed in detail. Shall include, lifting, transportation and installation requirements.
104 | Callout | 83 | Joon Cho | shall be developed by section 24.1.1 of BMPS-M2
106 | Callout | 85 | Salman Almajed | Application of tack coat after binder course
107 | Callout | 85 | Joon Cho | BMPS-S3
108 | Callout | 85 | Salman Almajed | Road Cross-sections and Details BMPS-S-69015
112 | Callout | 86 | Joon Cho | clarify with BS requirements as per section 6.3.11 & 6.3.12 of BMPS-S3
114 | Callout | 86 | Joon Cho | 5.0 mm ? need to check as per section 6.3.3 of BMPS-S3
117 | Callout | 86 | Joon Cho | for Tack coat
118 | Callout | 86 | Joon Cho | BMPS-S3
119 | Callout | 86 | Joon Cho | MICRON
126 | Callout | 86 | Joon Cho | 60% as per section 6.3.4 of BMPS-S3
129 | Callout | 87 | Joon Cho | clarify with section 6.3.8 of BMPS-S3
130 | Callout | 88 | Joon Cho | Civil Standard Paving and Details BMPS-S-50805
133 | Callout | 88 | Joon Cho | 8 mm
137 | Callout | 89 | Joon Cho | 8 mm
140 | Callout | 89 | Joon Cho | 300 mm
142 | Callout | 89 | Joon Cho | 600 mm
143 | Callout | 89 | Salman Almajed | <Add> until the compressive strength has reached 70% of the specified strength, and for 14 days minimum
145 | Callout | 89 | Joon Cho | 20 mm
146 | Callout | 89 | Joon Cho | 20 mm as per BMPS-S-50805
147 | Callout | 89 | Salman Almajed | 14 days.
150 | Callout | 89 | Joon Cho | 1/4 depth of the paving thickness as per BMPS-S-50805