## 000-Q-STD-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Erwin.Lugue | Check dimension
2 | Cloud+ | 1 | Erwin.Lugue | Check minimum bolt spacing
3 | Text Box | 1 | giovanny.rodriguez | CORRECT FILLET WELD SYMBOL
4 | Cloud+ | 1 | MAK | Delete
5 | Callout | 1 | Chandrahasan D | Description of Nz(Axia load??) and Vy(Shear??)
6 | Callout | 1 | Chandrahasan D | Description?
7 | Text Box | 1 | Erwin.Lugue | Design of anchorage shall be as per ACI-318 Chapter 17
8 | Cloud+ | 1 | Salman Almajed | Dimension text is not clear. Please move all dimension texts away from dimension lines (Typical comment).
9 | Cloud+ | 1 | Erwin.Lugue | Dimensions in mm
10 | Text Box | 1 | MAK | General Comment: All the texts in drawings shall be searchable and in UPPERCASE. Text fonts and styles shall be as per BMPS-A8.
11 | Callout | 1 | Erwin.Lugue | Missing dimensions
12 | Cloud+ | 1 | MAK | NTS
13 | Text Box | 1 | Salman Almajed | Nz (kN)
14 | Text Box | 1 | Erwin.Lugue | Provide the standard general notes and references
15 | Cloud+ | 1 | MAK | STANDARD DRAWING CONCRETE WORKS EMBEDDED PLATES TYPICAL DETAILS
16 | Text Box | 1 | Erwin.Lugue | There is not much of difference (besides extra width of 30mm) between types 2 & 3, types 4& 5
17 | Cloud+ | 1 | Erwin.Lugue | These are minimum embedded length
18 | Cloud+ | 1 | Erwin.Lugue | Verify minimum edge distances as per ACI-318, Chapter 17
19 | Callout | 1 | Chandrahasan D | Weld size to be included in the table