## 000-R-GAD-60006-001-RB-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | Page 1 | Bernard.Grace | Provide alternate emergency exit to building
2 | Callout | Page 1 | Bernard.Grace | Are the windows sized to permit evacuation in emergency
3 | Callout | Page 1 | Bernard.Grace | Glazing to permit monitoring of personel
4 | Callout | Page 1 | Bernard.Grace | Ensure 800 mm of free space from swing of door to edge of landing to ensure personnel are not forced back down the stairs
5 | Callout | Page 1 | Bernard.Grace | for Owner use or Conrtractor?
6 | Callout | Page 1 | Bernard.Grace | Air curtain to reduce entry of dust
7 | Callout | Page 1 | Bernard.Grace | Cesspit to be used to retain all waste for disposal via tankers to sewage treatment plant. No fluids are to be discharged to surrounding area
8 | Callout | Page 1 | Bernard.Grace | Consideration of firewall and sound proofing required to protect personnel within building.
9 | Callout | Page 1 | Bernard.Grace | Ensure appropriate measures such as concrete base slab and bund are utilised to mitigate potential fuel spills and protect environment
10 | Callout | Page 1 | Bernard.Grace | Fire fighting capabilities and fire rating of facilities to be identified. Ensure compliance to API RP 753 for portable buildings (such as portacabins, trailers) and to comply with Chevron Fire Protection Manual Appendix H-Building Sitting Assessments (FPM 6000H, issue 2007 or later, as applicable) Ref Document SS/370/PSM/425/SH which is included in Volume 3 of ITB document
11 | Callout | Page 1 | Bernard.Grace | Provide details on intended locations?
12 | Text Box | Page 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
13 | Call-out | Page 1 | MAK | Fill in EX and PN nos.
14 | Text Box | Page 1 | MAK | 000 - COMMON
15 | Call-out | Page 1 | MAK | Enter 002 in all sheets