## 000-R-GAD-60006-002-RB-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Bernard.Grace | Fire fighting capabilities and fire rating of facilities to be identified. Ensure compliance to API RP 753 for portable buildings (such as portacabins, trailers) and to comply with Chevron Fire Protection Manual Appendix H-Building Sitting Assessments (FPM 6000H, issue 2007 or later, as applicable) Ref Document SS/370/PSM/425/SH which is included in Volume 3 of ITB document
2 | Callout | 1 | Bernard.Grace | Glazing to permit monitoring of personel
3 | Callout | 1 | Bernard.Grace | Consideration of firewall and sound proofing required to protect personnel within building.
4 | Callout | 1 | Bernard.Grace | Ensure appropriate measures such as concrete base slab and bund are utilised to mitigate potential fuel spills and protect environment
5 | Callout | 1 | Bernard.Grace | Cesspit to be used to retain all waste for disposal via tankers to sewage treatment plant. No fluids are to be discharged to surrounding area
6 | Callout | 1 | Bernard.Grace | Ensure 800 mm of free space from swing of door to edge of landing to ensure personnel are not forced back down the stairs
7 | Callout | 1 | Bernard.Grace | Air curtain to reduce entry of dust
8 | Callout | 1 | Bernard.Grace | Are the windows sized to permit evacuation in emergency
9 | Callout | 1 | Bernard.Grace | Provide alternate emergency exit to building
10 | Callout | 1 | Bernard.Grace | Provide details on intended locations?
11 | Call-out | 1 | MAK | These are references to what?