## 000-R-GAD-60008-001-RB-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Bernard.Grace | Cesspit to be used to retain all waste for disposal via tankers to sewage treatment plant. No fluids are to be discharged to surrounding area
2 | Callout | 1 | Bernard.Grace | Fire fighting capabilities and fire rating of facilities to be identified. Ensure compliance to API RP 753 for portable buildings (such as portacabins, trailers) and to comply with Chevron Fire Protection Manual Appendix H-Building Sitting Assessments (FPM 6000H, issue 2007 or later, as applicable) Ref Document SS/370/PSM/425/SH which is included in Volume 3 of ITB document
3 | Callout | 1 | Bernard.Grace | Ensure appropriate measures such as concrete base slab and bund are utilised to mitigate potential fuel spills and protect environment
4 | Callout | 1 | Bernard.Grace | Ensure 800 mm of free space from swing of door to edge of landing to ensure personnel are not forced back down the stairs
5 | Callout | 1 | Bernard.Grace | Air curtain to reduce entry of dust
6 | Callout | 1 | Bernard.Grace | Ensure appropriate measures such as concrete base slab and bund are utilised to mitigate potential fuel spills and protect environment
7 | Callout | 1 | Bernard.Grace | Consideration of firewall and sound proofing required to protect personnel within building.
8 | Callout | 1 | Bernard.Grace | Provide details of intended locations
9 | Call-out | 1 | MAK | 1
10 | Call-out | 1 | MAK | If this drawing is common, why is assigned to Unit 018??
11 | Call-out | 1 | MAK | General Comment: It's preferred to enter the long form of Unit Name, unless the the field is short. Refer to the Homogenization Procedure for the correct Unit No., Name and format. 018 - NO. 1 RESIDUE HYDROCRACKING UNIT or 018 - 1RHCU
12 | Text Box | 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
13 | Call-out | 1 | MAK | Fill in EX and PN nos.