## 000-R-MST-50002-001-RB
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Antony.Bentley | General: It appears that this document is an updated replacement for doc. ref. 000-R-MST-60001-001 - "Technical Specification for Temporary Construction Facilities (Prefabricated or Modularized Buildings) Including Utilities" as such all review comments made on that document should be incorporated accordingly & the related comment spreadsheet returned completed
2 | Callout | 1 | Bernard.Grace | Title documents appropriately, this is not a method statement, it is a list of requirements for subcontractor bid inquiry
3 | Callout | 4 | Bernard.Grace | Explain why this is reduced from 619 stated on Drawing Number 000-R-GAD-60002--001 Rev B
4 | Callout | 5 | Bernard.Grace | all waste to be tankered off site and disposed off through WWTP.
5 | Callout | 5 | Bernard.Grace | all waste to be tankered off site and disposed off through WWTP.
6 | Callout | 5 | Bernard.Grace | No sewage is to be discharged/released to earth
7 | Callout | 6 | Danut.Dragan | "story" to read "storey"
8 | Callout | 8 | Bernard.Grace | Include loading requirements on slab to accelerate response from subcontractor.
9 | Callout | 8 | Bernard.Grace | Include ventilation requirements for the raised floor?
10 | Callout | 8 | Bernard.Grace | What about access requirements in the case of floor drain blockages?
11 | Callout | 9 | Bernard.Grace | Clarify text?
12 | Callout | 9 | Bernard.Grace | Heavy duty non slip.c
13 | Callout | 9 | Bernard.Grace | To preclude vermin entry below buildings
14 | Callout | 11 | Bernard.Grace | furniture
15 | Callout | 11 | Bernard.Grace | on
16 | Callout | 11 | Bernard.Grace | their
17 | Callout | 14 | Bernard.Grace | positive pressure/negative pressure
18 | Callout | 17 | Bernard.Grace | Male, female and disabled
19 | Callout | 17 | Bernard.Grace | Qty to be defind in detailed design
20 | Callout | 17 | Bernard.Grace | What about access to underside for potential cleaning of pipework and ventilation of enclosed space
21 | Callout | 17 | Bernard.Grace | What about gas tank storage to remove risk and frequency of changing bottles
22 | Note | 18 | 300048 | Check the generator is located in a none hazardous area,and complies with NFPA specification is a over-speed device required ( Rig Saver ) and flame arrestor is a ESD valve required on the generator diesel line
23 | Callout | 18 | Bernard.Grace | in
24 | Callout | 18 | Bernard.Grace | including shade and fuel bund to stop any spillage, pollution (fuel, noise, vapour, fumes) of environment
25 | Note | 19 | 300048 | Check vendors O&M manual and comply with servicing running hours
26 | Callout | 21 | Bernard.Grace | at least two in the large ablution areas
27 | Callout | 21 | Bernard.Grace | fused
28 | Callout | 21 | Bernard.Grace | Weatherproof
29 | Callout | 21 | Bernard.Grace | Weatherproof
30 | Callout | 21 | Bernard.Grace | Weatherproof
31 | Text Box | 22 | Antony.Bentley | ?
32 | Callout | 23 | Bernard.Grace | Cesspits (no waste whether partially treated or not is permitted to be discharged to soil)
33 | Text Box | 23 | Antony.Bentley | designed
34 | Text Box | 23 | Antony.Bentley | of not less than
35 | Note | 27 | 300048 | what is the volume of the tank. Check water supply should come from a permanent supply refer to NFPA 24 stipulate how many hours of continuous use in the event of fire
36 | Callout | 36 | Bernard.Grace | 22.1-1
37 | Callout | 36 | Bernard.Grace | Where will this discharge to?
38 | Callout | 37 | Bernard.Grace | 22.2-1
39 | Callout | 37 | Bernard.Grace | 24.3-1
40 | Callout | 37 | Bernard.Grace | This not main Alba Haul Road
41 | Callout | 37 | Bernard.Grace | This is not Alba Haul Road!
42 | Callout | 38 | Bernard.Grace | 22.3-2
43 | Callout | 40 | Danut.Dragan | suppose to be Crossing Road detail for El / Instr / FO cables. Drawing is blurry, and it shall be titled in or out the drawing. Detail / section to be specified.
44 | Callout | 57 | Danut.Dragan | Contractor to confirm whether the Ingress Protection is IP55 or IP65.
45 |  | 85 | AutoCAD SHX Text | CAR SHELDED PARKING - ATTACHMENT M
46 |  | 85 | AutoCAD SHX Text | DETAIL
47 |  | 85 | AutoCAD SHX Text | PLAN VIEW
48 |  | 85 | AutoCAD SHX Text | SECTION VIEW
49 | Callout | 95 | Danut.Dragan | shall read "All TLC Closed Spaces ..." - that shall include Warehouse but exclude the sheltered warehouse area. Important for Instrument storage.
50 | Callout | 97 | Danut.Dragan | should read: "MAIN NETWORK CABLING ..."
51 | Callout | 98 | Danut.Dragan | Topology cannot be "vertical", Cabling arrangement can be vertical if there are related to multi-floors / multi-storey building(s). TLC's are all one storey.