## 000-R-TSP-50002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Bernard.Grace | Include all aspects, such as mechanical, electrical , instrumentation, fire, communications etc
2 | Callout | 1 | Bernard.Grace | Include all aspects of work/building tolerances
3 | Callout | 1 | Mahdi Ali | THIS DOCUMENT IS A BASIS OF DESIGN AND NOT A SPECIFICATION. THUS THE DOCUMENT TYPE SHALL BE 'BOD' AND NOT 'TSP'. CHANGE THE DOCUMENT NUMBER AND CHANGE ALL THE REFERENCES TO THIS DOCUMENT ACCORDIGNLY
4 | Text Box | 1 | Antony.Bentley | S
5 | Text Box | 4 | Antony.Bentley | Provide a site plan with the approximate locations of each building with TAG reference in Appendix
6 | Callout | 4 | Chandrahasan D | Include the list of buildings not covered by this standard (viz). -Pre Engineered Metal buildings? - Pump and process equipment shelters ? - Analyzer houses etc.
7 | Text Box | 4 | Antony.Bentley | A
8 | Text Box | 4 | Bader Abdulrahman | Technical
9 | Text Box | 4 | Antony.Bentley | provided
10 | Callout | 5 | Bernard.Grace | All Building Colour schemes to be submitted to OWNER for approval
11 | Callout | 5 | Bernard.Grace | BMPS-S1 Drainage Sewer Systems
12 | Callout | 5 | Bernard.Grace | BMPS-S2 Site Preparation, Clearing and Earthworks
13 | Callout | 6 | Bernard.Grace | 752
14 | Text Box | 8 | Antony.Bentley | BS EN 12878
15 | Text Box | 8 | Antony.Bentley | Specification for ancilliary components for masonry...
16 | Text Box | 8 | Antony.Bentley | Pigments....
17 | Text Box | 8 | Antony.Bentley | BS EN 13139
18 | Text Box | 8 | Antony.Bentley | It is understood that the BS list is taken directly from BMPS but a large number of these BS's are withdrawn or superseded by new codes - update to latest standard reference
19 | Text Box | 8 | Antony.Bentley | BS EN 197-1
20 | Text Box | 8 | Antony.Bentley | BS EN 12620
21 | Text Box | 8 | Antony.Bentley | BS 845-1
22 | Text Box | 8 | Antony.Bentley | BS EN 1008
23 | Text Box | 8 | Antony.Bentley | ETC.
24 | Text Box | 8 | Antony.Bentley | BS EN 459-1
25 | Text Box | 9 | Antony.Bentley | BS EN 842
26 | Text Box | 9 | Antony.Bentley | withdrawn
27 | Text Box | 9 | Antony.Bentley | BS EN 12056-3
28 | Text Box | 9 | Antony.Bentley | ETC.
29 | Text Box | 9 | Antony.Bentley | BS 9991
30 | Text Box | 9 | Antony.Bentley | -7
31 | Text Box | 9 | Antony.Bentley | BS 6100-6
32 | Text Box | 9 | Antony.Bentley | . General Requirements
33 | Text Box | 9 | Antony.Bentley | withdrawn
34 | Text Box | 9 | Antony.Bentley | BS EN 1935
35 | Text Box | 10 | Antony.Bentley | Other for...
36 | Text Box | 10 | Antony.Bentley | BS EN 197-1
37 | Text Box | 10 | Antony.Bentley | ETC.
38 | Text Box | 10 | Antony.Bentley | BS EN 197-1
39 | Text Box | 10 | Antony.Bentley | Withdrawn
40 | Text Box | 10 | Antony.Bentley | -7
41 | Text Box | 10 | Antony.Bentley | ETC.
42 | Text Box | 10 | Antony.Bentley | -1
43 | Text Box | 11 | Antony.Bentley | ISO 10595
44 | Text Box | 11 | Antony.Bentley | Withdrawn
45 | Text Box | 11 | Antony.Bentley | BS EN 933
46 | Text Box | 11 | Antony.Bentley | ETC.
47 | Text Box | 11 | Antony.Bentley | BS EN 1008
48 | Text Box | 11 | Antony.Bentley | ISO 10581
49 | Text Box | 11 | Antony.Bentley | BS EN 197-1
50 | Text Box | 11 | Antony.Bentley | Other for...
51 | Text Box | 11 | Antony.Bentley | BS EN 14411
52 | Text Box | 12 | Antony.Bentley | BS EN 13964
53 | Text Box | 13 | Antony.Bentley | BS EN 13279-1
54 | Text Box | 13 | Antony.Bentley | 14749
55 | Text Box | 13 | Erwin.Lugue | Missing standards for: - Plumbing and drainage - Sanitary Fittings & Fixtures
56 | Text Box | 13 | Antony.Bentley | BS 8417
57 | Text Box | 13 | Antony.Bentley | BS EN 13164
58 | Text Box | 13 | Antony.Bentley | withdrawn
59 | Text Box | 13 | Antony.Bentley | BS EN 197-1
60 | Text Box | 13 | Antony.Bentley | ETC.
61 | Text Box | 13 | Antony.Bentley | BS EN 942
62 | Text Box | 13 | Antony.Bentley | repeated from above
63 | Text Box | 13 | Antony.Bentley | BS EN 13162
64 | Text Box | 14 | Antony.Bentley | withdrawn
65 | Callout | 14 | Bernard.Grace | floor areas around equipment are to be marked to denote areas of safe passage etc.
66 | Callout | 14 | Bernard.Grace | provide value
67 | Callout | 14 | Bernard.Grace | Include access for vehicles, parking and maintenance loading points as required
68 | Text Box | 14 | Antony.Bentley | BS ISO 3864
69 | Callout | 14 | Joon Cho | The Buildings shall be accessible by roads of required widths.
70 | Callout | 14 | Chandrahasan D | Architects&
71 | Callout | 14 | Bernard.Grace | Include main design factors: Steel framed, Reinforced concrete (Blast Resistant and non-blast resistant). ingress and egress etc
72 | Callout | 14 | Chandrahasan D | Suggested to include minimum area requirement for each room(usage) type
73 | Callout | 14 | Bernard.Grace | Include electrical, mechanical, drainage, sanitation, security, health & safety criteria, fire detection/protection
74 | Callout | 15 | Bernard.Grace | ease
75 | Callout | 15 | Joon Cho | not necessary
76 | Callout | 15 | Joon Cho | <Add> para. 6.1.25, 6.1.26 & 6.1.27 in BMPS-R1 shall be added
77 | Text Box | 15 | Antony.Bentley | The use of precast construction..
78 | Callout | 15 | Bernard.Grace | include blast considerations on structure and elevated slabs for substations. Single storey preferable with 2 storey offices and overhead cranes in Maintenance Workshop
79 | Strikethrough | 15 | Joon Cho | In any case design loads are to be in accordance with BMPS-A1.
80 | Callout | 15 | Bernard.Grace | No HVAC plant is to be located on roofs
81 | Callout | 15 | Bernard.Grace | use
82 | Callout | 15 | Joon Cho | <Add> para. 6.2.1 b) of BMPS-R1 shall be added.
83 | Callout | 15 | Chandrahasan D | Suggested to include building siting considerations (offset from road and spaces around buildings etc) to be given in Architectural design
84 | Callout | 16 | Joon Cho | considered in accordance with the Project Specification of 'BOD' (Doc......) and para. 6.2.2 of BMPS-R1
85 | Cloud+ | 16 | Salman Almajed | Use superscript for "2" (typical comment)
86 | Strikethrough | 16 | Joon Cho | as stated in “BMPS-A1 Basic Engineering Design Data”, “BMPS-M1 Basic Civil and Structural Design Data” and “BMPS-M2 Concrete Structures”.
87 | Callout | 16 | Chandrahasan D | Identify Light and heavy storage areas clearly
88 | Text Box | 16 | Salman Almajed | <Add> Satellite rack room - 5.00 kN/m2 (According to BMPS-R2, sec. 6.2.7)
89 | Text Box | 17 | Antony.Bentley | loading
90 | Callout | 17 | Bernard.Grace | T1849: - Electrical Substations as a minimum shall be designed as Blast Resilient. Electrical Substations outside blast zone shall be designed as Blast Resilient. Main Substation and any other Substation within Blast Zone feeding more than one Unit shall be designed as Blast Resistant. Electrical Substation within Blast Zone of the adjacent unit or affected by blast occurred from adjacent/surrounding unit shall be designed as Blast Resistant.
91 | Callout | 17 | Sankara | Substation numbers to be updated to BMPS A8
92 | Callout | 17 | Mahdi Ali | REFER TO THE LATEST MOM SIGNED WITH REFERENCE TO THE TAGGING FOR BUILDINGS, SUSBTATIONS AND SATELLITE RACK ROOMS. REFER TO THE LATEST EDITION OF BMPS-A8
93 | Callout | 17 | Erwin.Lugue | Only in S.I. units
94 | Callout | 17 | Bernard.Grace | 181BLD01
95 | Cloud+ | 17 | Erwin.Lugue | Blast Loads
96 | Callout | 17 | Bernard.Grace | Contractor to submit risk assessment of buildings for owner approval
97 | Cloud+ | 17 | Erwin.Lugue | Provide S.I. units, refer to BPMS-A1
98 | Text Box | 17 | Antony.Bentley | will
99 | Callout | 17 | Bernard.Grace | T1849: - Electrical Substations as a minimum shall be designed as Blast Resilient. Where Substations house critical equipment, or where damage to the building will lead to escalation events (including but not limited to loss of power to adjacent unit), then the Substation shall be Blast Resistant. The final design requirements shall be established through a risk assessment, and approved by the Owner, during the Detailed Design phase. This is applicable to all BMP substations.
100 | Cloud+ | 18 | Erwin.Lugue | Provide S.I. units as per BPMS-A1
101 | Cloud+ | 19 | Erwin.Lugue | Provide S.I. units as per BPMS A1
102 | Text Box | 19 | Antony.Bentley | & in accordance with BMPS-R8.
103 | Callout | 19 | Bernard.Grace | Disability provisions
104 | Callout | 19 | Bernard.Grace | Where is TTSJV risk assessment complete with blast impact on buildings for OWNER approval?
105 | Callout | 20 | Bernard.Grace | Include all buildings
106 | Callout | 20 | Bernard.Grace | Include manning values to confirm sanitary appliances and as part of escape criteria
107 | Callout | 20 | Bernard.Grace | The building Tag should read 041BLD01, 018BLD01 etc
108 | Callout | 21 | Bernard.Grace | Include manning values to confirm sanitary appliances and as part of escape criteria
109 | Text Box | 22 | Salman Almajed | <Add> All buildings to be provided with shaded car park. The number of parking lots shall match the number of offices and personnel of each building. (refer T1473 & T737)
110 | Callout | 22 | Bernard.Grace | Include manning values to confirm sanitary appliances and as part of escape criteria
111 | Text Box | 22 | Antony.Bentley | ?
112 | Callout | 22 | Joon Cho | <Add> section 6.3 Safety of BMPS-R1 shall be added
113 | Callout | 22 | Joon Cho | , even if it is an unmanned building,
114 | Callout | 22 | Joon Cho | Positive pressurized, JV to confirm
115 | Callout | 23 | Bernard.Grace | the
116 | Cloud+ | 23 | Erwin.Lugue | The satellite rack rooms shall be designed to allow 20% spare space for cabinets- BPMS-R2 sec 6.1.4
117 | Callout | 23 | Bernard.Grace | Ensure compliance with BMPS R2 6.2.3 or Technical querry inf deviation is required
118 | Callout | 23 | Joon Cho | <Add 6.2.5> section 6.3 Safety of BMPS-R2 shall be added.
119 | Cloud+ | 24 | Erwin.Lugue | Refer to BPMS-R1 sec. 7.2.1.c & BPMS-R3 sec 7.2.4
120 | Callout | 24 | Bernard.Grace | Include tolerance levels for concrete slab(+-6mm etc)
121 | Callout | 24 | Bernard.Grace | Please review this statement and confirm if TTSJV is going to provide all substations as blast resistant.
122 | Callout | 24 | Sankara | Clarify the basis of this philosphy.
123 | Callout | 24 | Bernard.Grace | storey
124 | Text Box | 24 | Antony.Bentley | ?
125 | Callout | 24 | Sankara | This statement needs to be re-written to avoid ambiguity.
126 | Callout | 25 | Joon Cho | <Add 6.3.5> section 6.3 of BMPS-R3 shall be added.
127 | Text Box | 25 | Antony.Bentley | Building
128 | Callout | 25 | Bernard.Grace | All the facilities of the building shall be accessible to people with physical disabilities. The building shall be provided with necessary facilities for disabled people such as toilets, access, etc. as per latest Owner approved international and local standards and regulations. BMPS-R4 6.1.11
129 | Text Box | 25 | Antony.Bentley | 6
130 | Callout | 26 | Salman Almajed | Add para. 7.2.11 of BMPS-R4
131 | Text Box | 26 | Antony.Bentley | plasterboard on steel framed stud system
132 | Text Box | 27 | Sankara | The new laboratory shall have an air conditioned electrical room with outdoor transformers.
133 | Callout | 27 | Bernard.Grace | Laboratory to remain operational throughout works
134 | Callout | 27 | Bernard.Grace | on the south side of the building will be provided
135 | Callout | 28 | Bernard.Grace | External Doors, office doors vision panels, roller shutter doors (BMPS- R1 7.5.4.1 & 2) with pedestrian access panels. Windows.
136 | Callout | 28 | Bernard.Grace | numerous overhead cranes,
137 | Callout | 28 | Bernard.Grace | Include details on the measures taken to protect the steel from impact of moving vehicles/loads, especially at the service bay areas
138 | Callout | 28 | Bernard.Grace | office floors above the workshop offices for
139 | Callout | 28 | Bernard.Grace | Enhance this description to provide details of what influenced the office complex and workshop area, including lifts, overhead cranes, zoning of areas, delineation of space
140 | Callout | 28 | Bernard.Grace | Please clarify the extent of air conditioning within the building. Office areas air conditioned and workshop areas ventilated?
141 | Text Box | 28 | Hasan Asad | As per FEED design, elevators should be provided.
142 | Callout | 28 | Bernard.Grace | s
143 | Callout | 28 | Bernard.Grace | Access considerations, floor finishes,( high impact in servicing areas, office considerations, toilets, disabled provisions etc
144 | Callout | 28 | Bernard.Grace | What considerations were given to any wall/roof light transmitting panels and subsequent access to roof to permit cleaning and servicing of fans etc.
145 | Text Box | 29 | Antony.Bentley | Please differentiate between 'new' CB's & revamp 'CB's'
146 | Callout | 29 | Bernard.Grace | positively
147 | Callout | 29 | Sankara | All batteries shall be Ni Cd type, as per BMPS. No wet cells are envisaged.
148 | Callout | 30 | Bernard.Grace | 100 % redundancy of systems (HVAC, electrical, emergency generator to ensure survival and ability to function in the event of an incident. Shaded car parking.
149 | Callout | 30 | Bernard.Grace | including HVAC Fire Dampers
150 | Callout | 30 | Bernard.Grace | Outline/Provide the criteria used to design the building
151 | Callout | 30 | Bernard.Grace | This building probably warrants its own design basis
152 | Callout | 30 | Bernard.Grace | Antistatic flooring utilised as required
153 | Callout | 30 | Bernard.Grace | Telecoms room, HVAC room, simulator room, toilets, disabled facilities, conference room, UPS, Battery Room, etc
154 | Callout | 30 | Bernard.Grace | Interior finishes shall have a flame spread rating no greater than 50, as defined by 'NFPA 255 (or ASTM E84) Test Methods Surface Burning - Building Materials' BMPS-R& 6.12
155 | Callout | 30 | Bernard.Grace | positively
156 | Callout | 30 | Bernard.Grace | Glazing is to be utiilized to ease monitoring of works by office / supervisor personnel
157 | Callout | 30 | Bernard.Grace | All batteries shall be Ni Cd type, as per BMPS. No wet cells are envisaged.
158 | Callout | 31 | Bernard.Grace | Internal insulation in walls where sound reduction is required between rooms, the insulation shall contribute to the overall construction achieving a sound reduction of 55dB or better. BMPS-R1 7.2.1.g and BMPS-R7 6.8)
159 | Text Box | 31 | Sankara | Include Electrical Room in Operations Building
160 | Callout | 32 | Bernard.Grace | with a minimum thermal value of 0.35W/m2C
161 | Callout | 32 | Joon Cho | in Table 1 of BMPS-B5
162 | Text Box | 32 | Erwin.Lugue | Colour schemes shall be submitted for owner approval
163 | Text Box | 32 | Bader Abdulrahman | storey
164 | Callout | 32 | Bernard.Grace | this
165 | Callout | 32 | Bernard.Grace | please explain?
166 | Text Box | 33 | Erwin.Lugue | Indicate requirement for thickened slabs
167 | Text Box | 33 | Erwin.Lugue | type of blocks or CMU?
168 | Text Box | 33 | Erwin.Lugue | Wall plastering & finishes?
169 | Callout | 34 | Erwin.Lugue | with bird wire net
170 | Text Box | 34 | Erwin.Lugue | Thermal conductivity requirements (U)?
171 | Text Box | 36 | Hasan Asad | Maintenance Workshop doors should be motorized with manual operation as alternative.
172 | Callout | 37 | Erwin.Lugue | Shall be powder coated. Refer to BPMS-R1 sec 7.6.4.c
173 | Callout | 38 | Erwin.Lugue | Indicate flame spread rating
174 | Callout | 38 | Bernard.Grace | Stipulate floor tolerances especially for floors housing equipment (Substations +-???mm)
175 | Callout | 38 | Bernard.Grace | Ensure samples and mock ups are presented for OWNER approval
176 | Text Box | 39 | Erwin.Lugue | Load capacity of raised floor system?
177 | Text Box | 39 | Erwin.Lugue | Painting, & coating?
178 | Text Box | 39 | Erwin.Lugue | Type of suspension system & load rating Requirements for fire/smoke safety
179 | Callout | 39 | Joon Cho | para 8.6.10.1 loading in BMPS-R1 shall be referred
180 | Callout | 40 | Bernard.Grace | Disabled access and egress complete with handrails
181 | Text Box | 40 | Erwin.Lugue | Surface finishes of ramps & walkways?
182 | Text Box | 40 | Erwin.Lugue | Walkways?
183 | Callout | 41 | Bernard.Grace | Mock-up of proposed finishes to be presented for Owner acceptance/approval
184 | Cloud+ | 42 | Erwin.Lugue | Anti-slip & anti acid ceramic tiles as per FEED BRA-232729. Verify.
185 | Cloud+ | 42 | Erwin.Lugue | Verify AC-UPS wall finish as per FEED BRA-23279
186 | Callout | 42 | Bernard.Grace | Reinforced concrete slab is stipulated in para 6.3.3 of tis document
187 | Callout | 42 | Bernard.Grace | Include details for finishing openings through slab for cable entry
188 | Cloud+ | 42 | Erwin.Lugue | No skirting?
189 | Callout | 43 | Bernard.Grace | Thick quilted, prayer carpet
190 | Callout | 43 | Bernard.Grace | Anti fungal paint
191 | Callout | 43 | Bernard.Grace | C3 for ceiling?
192 | Callout | 43 | Bernard.Grace | Anti fungal paint
193 | Callout | 44 | Bernard.Grace | C3 for ceiling?
194 | Callout | 44 | Bernard.Grace | Anti fungal paint
195 | Callout | 44 | Bernard.Grace | Thick quilted, prayer carpet
196 | Callout | 45 | Bernard.Grace | Include finishes for all other buildings or stipulate information to be provided later etc? Laboratory, Maintenance Workshop with Offices, Public Toilet Block, Control Rooms etc
197 | Callout | 46 | Bernard.Grace | & non slip
198 | Callout | 46 | Bernard.Grace | Painted
199 | Callout | 46 | Bernard.Grace | Define finish for section between substation and transformers (concrete blockwork or reinforced concrete) BMPS-R3 6.1.31
200 | Callout | 46 | Bernard.Grace | & non slip
201 | Callout | 46 | Bernard.Grace | & non slip