## 000-S-STD-50003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | Delete
2 | Text Box | 1 | Salman Almajed | Add description for the drawings
3 | Text Box | 1 | Salman Almajed | BMPS-Q-50701
4 | Text Box | 1 | Antony.Bentley | INSITU
5 | Callout | 1 | Chandrahasan D | Verify the suitablity of material for the type of service and the environment it will be exposed.
6 | Text Box | 1 | Antony.Bentley | It is unclear as to what these dims relate to, what is relevance of the cover thicknesses, internal radii - enlarge detail & clarify to show cover bedding detail - as S1-14.4.4
7 | Text Box | 1 | Antony.Bentley | SI units
8 | Text Box | 1 | Salman Almajed | BMPS-S-50806
9 | Text Box | 1 | Erwin.Lugue | Around pipe openings shall have similar additional detail in wall reinforcement
10 | Text Box | 1 | Antony.Bentley | LAID ON BITUMEN IMPREGNATED FIBRE ROPE
11 | Callout | 1 | Erwin.Lugue | Not a recommended pipework installation
12 | Cloud+ | 1 | MAK | NTS
13 | Cloud+ | 1 | MAK | Text style and height should not be changed. Every border has predefined styles and heights and shall be used as outline in BMPS-A8.
14 | Text Box | 1 | MAK | General Comment: All the texts in drawings shall be searchable and in UPPERCASE. Text fonts and styles shall be as per BMPS-A8.
15 | Callout | 1 | Salman Almajed | <Remove>
16 | Cloud+ | 1 | MAK | 000 - COMMON
17 | Callout | 1 | Erwin.Lugue | Vents to be located downwind, away from sources of ignition or equipments
18 | Text Box | 1 | Antony.Bentley | 14) IN AREAS SUBJECTED TO HIGH WATER TABLE LEVELS THE MANHOLES SHALL BE CHECKED FOR BUOANCY EFFECTS TO CONFIRM STRUCTURAL THICKNESSES.
19 | Cloud+ | 1 | MAK | Move to 2nd line of the title
20 | Text Box | 1 | Salman Almajed | HYDROPHILIC
21 | Callout | 1 | Erwin.Lugue | Ensure gas seal between inlet and outlet as per BPMS-SD-S-10279
22 | Callout | 1 | Joon Cho | Work scope shall be cleared (typical comment)
23 | Text Box | 1 | Antony.Bentley | Needs to be deeper to provide cover to lifting bar when filled with s/c
24 | Text Box | 1 | Antony.Bentley | See S1-14.4.6
25 | Callout | 1 | Erwin.Lugue | Remove this circle
26 | Text Box | 1 | Antony.Bentley | Additional detail to be added to show reducing slab & shaft after depth of 3.3m see S1-14.4.2
27 | Cloud+ | 1 | Salman Almajed | <Recommendation> Please use closed stirrups or provide a better arrangement. (Typical comment)
28 | Text Box | 1 | Antony.Bentley | SI units
29 | Text Box | 1 | Antony.Bentley | SPECIFY SIZE & TYPE
30 | Cloud+ | 1 | Erwin.Lugue | For vent details, refer to BPMS-SD-S-10279
31 | Text Box | 1 | Salman Almajed | HYDROPHILIC
32 | Callout | 1 | Joon Cho | Min. 3,700 mm shall be confirmed (typical comment)
33 | Callout | 1 | Salman Almajed | The detail shows two diameters for stirrups. Please remove one of them (Typical comment).
34 | Text Box | 1 | Antony.Bentley | MIN.
35 | Text Box | 1 | Antony.Bentley | Add all standard detail drawings in this transmittal
36 | Text Box | 1 | Antony.Bentley | Correct spelling (typ)
37 | Callout | 1 | Chandrahasan D | Verify the requirement of pipe material specification in standard dwg. If required to be shown in standard dwg, make sure the connection details are available for other type of pipe materials.
38 | Text Box | 1 | Antony.Bentley | FOR WHAT? REBAR SHOWN IN ELEVATION
39 | Text Box | 1 | Erwin.Lugue | Ensure that all the manholes are adequately designed without excessive settlement & checked for uplift (if necessary)
40 | Text Box | 1 | Antony.Bentley | SI UNITS
41 | Text Box | 1 | Antony.Bentley | Confirm Note no. & tidy text
42 | Callout | 1 | Chandrahasan D | specify the bedding material for cover slab
43 | Text Box | 1 | Antony.Bentley | Y