## 000-S-STD-50004-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Erwin.Lugue | Covers shall be designed as per the minimum loads mentioned in BPMS A1 sec 10.7.10
2 | Cloud+ | 1 | MAK | 000 - COMMON
3 | Cloud+ | 1 | Erwin.Lugue | The detail is more of a cast-in place
4 | Text Box | 1 | Salman Almajed | BMPS-S-50806
5 | Callout | 1 | Salman Almajed | The detail shows two diameters for stirrups. Please remove one of them (Typical comment).
6 | Callout | 1 | Erwin.Lugue | Specify piping material
7 | Text Box | 1 | Erwin.Lugue | Ensure that all the manholes are adequately designed without excessive settlement & checked for uplift (if necessary)
8 | Cloud+ | 1 | MAK | Move to 2nd line of the title
9 | Cloud+ | 1 | MAK | Text style and height should not be changed. Every border has predefined styles and heights and shall be used as outline in BMPS-A8.
10 | Text Box | 1 | Antony.Bentley | General note: All comments made on drawing no. 50003-001 are applicable to the similar details on this sheet
11 | Text Box | 1 | MAK | General Comment: All the texts in drawings shall be searchable and in UPPERCASE. Text fonts and styles shall be as per BMPS-A8.
12 | Callout | 1 | Salman Almajed | Please add 4th re-bar or modify stirrup arrangement.
13 | Cloud+ | 1 | MAK | NTS
14 | Cloud+ | 1 | MAK | Delete
15 | Text Box | 1 | Salman Almajed | Add description for the drawings
16 | Callout | 1 | Joon Cho | TOP elevation of multiple inlet lines in this chamber shall be lower than BOP of outlet lines for Gas seals. Contractor to confirm (typical comment)
17 | Text Box | 1 | Salman Almajed | BMPS-Q-50701
18 | Callout | 1 | Joon Cho | No vent pipe in this chamber, it shall be clarified whether the vent pipe shall be provided per each chamber or not. (typical comment)
19 | Text Box | 1 | Erwin.Lugue | Around pipe openings shall have similar additional detail in wall reinforcement