## 000-S-TSP-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Antony.Bentley | General comment : If a separate document isn't being provided the hydraulic input into the design of the drainage basin should be described within this document
2 | Text Box | 2 | Antony.Bentley | to match title on Cover sheet
3 | Text Box | 4 | Antony.Bentley | Document reference
4 | Callout | 4 | Salman Almajed | Why is this highlighted?
5 | Text Box | 5 | Antony.Bentley | FHWA-HIF-12-026 HDS No.5
6 | Callout | 6 | Salman Almajed | <Add> BMPS-S3 Roads and Paved Areas
7 | Text Box | 7 | Joon Cho | <Add> Plant Datum & Coordinate System Dwg.No. 000-A-PPN-60006-001 IFC Rev.0
8 | Text Box | 8 | Antony.Bentley | Add statement to say TCF area is not incl. within this BOD or clarify how it is to be designed
9 | Text Box | 8 | Antony.Bentley | In this section include a description of the SOW for each OC with a sketch plan in an Appendix showing the boundaries of scope.
10 | Text Box | 8 | Chandrahasan D | Rearrange this table to show minimum vertical and horizontal clearance between different U/G utilities & structures.
11 | Text Box | 8 | Antony.Bentley | s
12 | Text Box | 8 | Antony.Bentley | sources
13 | Callout | 8 | Joon Cho | Which criteria has been referred ? Contractor to clarify
14 | Callout | 9 | Bernard.Grace | There is clean water and contaminated water and both should be defined and described in this section.
15 | Text Box | 10 | Joon Cho | <Add> Process waste water should not enter these sewers upstream of the diversion point, unless flow from the source can be eliminated when the storm water stream is being diverted.
16 | Callout | 10 | Salman Almajed | <Add> subjected to owner's approval.
17 | Callout | 10 | Salman Almajed | 13
18 | Callout | 10 | Bernard.Grace | are
19 | Text Box | 10 | Antony.Bentley | In each of the above 10.1 to 10.3 the system is discharged to separate compartments within the the water retention basin, add brief explanation under each or add 10.4 Drainage Basin
20 | Text Box | 10 | Antony.Bentley | Under this section include appendix reference and add simple layout sketches indicating the layout for each system including catchment & point of discharge
21 | Callout | 10 | Bernard.Grace | will
22 | Text Box | 11 | Chandrahasan D | Double Sealed cover for OWS application
23 | Text Box | 11 | Antony.Bentley | Expand to describe the system: local collection, pumped to common chamber, pumped to STP on site/offsite etc.
24 | Text Box | 11 | Antony.Bentley | external blind sump or is each tx bund used to contain spilages
25 | Text Box | 11 | Erwin.Lugue | Include the requirements for separators, sewage treatment & wastewater disposal as required
26 | Text Box | 11 | Erwin.Lugue | Provision for caustic, acid drains, neutralization & other special sewer systems if required
27 | Text Box | 14 | Joon Cho | , where necessary, shall be bitumen or concrete lined
28 | Callout | 14 | Salman Almajed | <Add> except for large bunded areas (eg large crude tankage) in areas of frequent and high-intensity rainfall, the Owner may require that the offsite CSS design capacity is based on the simultaneous rainfall and firewater flow rate loads. (BMPS-S1 sec. 10.3.1)
29 | Text Box | 14 | Antony.Bentley | Add short section to explain how the same systems are designed within TCF or advise where this is addressed
30 | Text Box | 14 | Antony.Bentley | catchments
31 | Callout | 14 | Joon Cho | Contractor to clarify with whether 1/360 or 0.002778
32 | Text Box | 14 | Erwin.Lugue | Verify if there are any peak load factor applied
33 | Cloud+ | 15 | Erwin.Lugue | Provide in S.I. units K=0.0195
34 | Cloud+ | 16 | Erwin.Lugue | Repeated. Calculation of velocity should be referred to sec 12.6.2
35 | Text Box | 17 | Antony.Bentley | (12.2 L/min.m2)
36 | Text Box | 17 | Antony.Bentley | 880 m3/hr (4 x 220)
37 | Text Box | 17 | Antony.Bentley | 960 m3/hr (880 x 1.1)
38 | Text Box | 17 | Antony.Bentley | Are there any such areas, if so name them with Unit no., if not then remove paragraph.
39 | Text Box | 17 | Antony.Bentley | Delete: Code referenced is not contained/recognised within BMPS's
40 | Text Box | 17 | Antony.Bentley | In accordance with BMPS-S5 7.1.4 the maximum fire water demand is based on the worst fire scenario taking into account the fire water required for the fire pool plus the cooling of the adjacent equipment. The BMP units drainage systems will be provided with catch basins serving segregated rectangular shapes with a maximum area of 300m2
41 | Callout | 18 | Julio.Aguilar | How using the Appendix I of BMPS-A1 can the flow rates be determined. Explain
42 | Text Box | 18 | Erwin.Lugue | Individual catchbasin capacities shall be designed with the minimum capacities as stated in BPMS S1 sec 10.2.2
43 | Text Box | 18 | Antony.Bentley | Table 1 within
44 | Text Box | 20 | Erwin.Lugue | Provide the criteria for quantifying head losses in manholes & fittings
45 | Cloud+ | 21 | Julio.Aguilar | Water
46 | Callout | 22 | Joon Cho | Trench ?
47 | Cloud+ | 22 | Julio.Aguilar | Water
48 | Callout | 23 | Joon Cho | please correct proper description
49 | Callout | 23 | Salman Almajed | Repeated in para. 10.5
50 | Callout | 23 | Erwin.Lugue | Sealing of pipe sleeves shall be as per BPMS-S-3961-13_0