## 005-A-HZR-00001-001-R0-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | MAK | General Comment: For the correct Unit No. and Name Format, refer to Homogenization Procedure.
2 | Call-out | 1 | MAK | Delete
3 | Text Box | 1 | Julio.Aguilar | Ensure use of the project finalized cover page for this document following the homogenization procedure.
4 | Text Box | 1 | MAK | 005 - C3/C4 LPG STORAGE FACILITY AT REFINERY
5 | Text Box | 1 | seongjin.lee | Note: This transmittal is hereby returned with Code 2. As per the agreed plan with SOC, OWNER comments will be captured in a joint review meeting and recorded as Minutes of Meetings. However the approval code may be changed according to the result of the review meeting
6 | Call-out | 3 | Mahdi Ali | ALWAYS QUOTE BAPCO NUMBERS
7 | Call-out | 4 | MAK | Move this section to top
8 | Text Box | 7 | MAK | Attachment 1 - HAZOP 2 General Parameter Node Worksheet
9 | Call-out | 7 | Mahdi Ali | BMPS-A-50003
10 | Text Box | 7 | MAK | Bapco Doc. No.: 005-A-HZR-00001-001 Page: 7/20
11 | Call-out | 7 | MAK | General Comment: Add this information to every page of the attachment.
12 | Call-out | 7 | MAK | General Comment: Add the title to every page of the attachment.
13 | Callout | 7 | Julio.Aguilar | Resolution to be discussed during PID review meeting. Adequate drain and vent to be covered for all vents and drain through all unit 005 PIDs.
14 | Call-out | 7 | Mahdi Ali | QUOTE BAPCO NUMBER
15 | Call-out | 8 | Mahdi Ali | QUOTE BAPCO NUMBER
16 | 텍스트 상자 | 9 | User | 9
17 | Text Box | 10 | MAK | Bapco Doc. No.: 005-A-HZR-00001-001 Page: 10/20
18 | Call-out | 10 | MAK | General Comment: Add the title to every page of the attachment.
19 | Call-out | 10 | MAK | General Comment: Add this information to every page of the attachment.
20 | Text Box | 10 | MAK | Attachment 2 - HAZOP 2 Specific Parameter Node Worksheet
21 | Callout | 12 | Julio.Aguilar | This Hazop recommendation shall not be closed without developing a surge analysis to ensure surge pressure will not be a problem during operations. SECL to confirm whether the surge analysis was developed.