## 005-A-PPN-55001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Joon Cho | 1. Datum point for this Unit 005 shall be specified. 2. IPMT recommend that SOC scope of work shall be identified and/or denoted by the Battery Limits or Unit Limits. 3. IPMT recommend that Road & Paving (Asphalt road/Concrete paving/Gravel paving) shall be identified. 4. IPMT recommend that appearance or outward shape for the mounded storage bullet shall be developed by mechanical data sheet. 5. All HOLD items or Issue Note for potential changes/revisions shall be specified.
2 | Callout | 1 | Robert.Kawitzki | 6500mm overhead clearance required to underside of steel required at road crossing
3 | Callout | 1 | Robert.Kawitzki | All Holds to be clouded
4 | Callout | 1 | Joon Cho | Basin inside dimension as per the requirement shall be denoted.
5 | Callout | 1 | JaiMun.Oh | C3/ C4 pumps and all are well vertically suspended pumps. Therefore monorail is not suitable for rigging subject pumps. Please provide individual removable roof for a crane to lift the pumps for maintenance.
6 | Callout | 1 | Robert.Kawitzki | Confirm drainage requirements
7 | Callout | 1 | Joon Cho | Curbed area shall be denoted by dimension
8 | Cloud+ | 1 | MAK | Delete second line of the title
9 | Cloud+ | 1 | MAK | Don't use FEED drawing numbers.
10 | Callout | 1 | Robert.Kawitzki | Ensure that pump suction line has no high points
11 | Text Box | 1 | MAK | General Comment: Use the latest drawing borders that are part of the Homogenisation Procedure.
12 | Callout | 1 | Joon Cho | Improper column location, SOC to re-check
13 | Callout | 1 | Robert.Kawitzki | Inspection tunnel to adhere to BMPS A4 5.5.4
14 | Callout | 1 | Robert.Kawitzki | Lines to reflect what is shown on drawing. Use different font to centerline
15 | Callout | 1 | Joon Cho | Location by the coordinates shall be specified or denoted
16 | Callout | 1 | Joon Cho | Min. requirements ? if any. SOC to confirm
17 | Callout | 1 | Joon Cho | No Handrail around Mounded bullet basin ? SOC to confirm
18 | Callout | 1 | Joon Cho | Piperack elevation view with vertical bracing bay, anchor bay, expansion joint if any shall be shown.
19 | Text Box | 1 | Aamer.Hubail | Provide davit for removal of storage vessel manways + advise method of removal of safety valves and control valves
20 | Callout | 1 | Joon Cho | Provisional dimension shall be denoted onto plan & section view respectively
21 | Cloud+ | 1 | MAK | Refer to BMPS-A8, Section 4.6.15 for the proper shelter equipment tag numbering.
22 | Cloud+ | 1 | MAK | Refer to BMPS-A8, Section 4.6.15 for the proper Shelter equipment tag numbering.
23 | Callout | 1 | Joon Cho | Shelter height to specify
24 | Callout | 1 | Robert.Kawitzki | Show staircase and missing equipment in sectional view
25 | Text Box | 1 | Salman Almajed | SOC to check and verify whether fence is required for LPG storage area. If fence is required, fence layout to be shown on this drawing.
26 | Callout | 1 | Joon Cho | SOC to clarify and to line off as per use of purpose
27 | Callout | 1 | Joon Cho | SOC to confirm the application limits on the top surface including the purpose of this concrete pad
28 | Callout | 1 | Mahdi Ali | THIS NOTE IS APPLICABLE FOR THE ENTIRE DRAWING: AVOID THE USE OF WORD 'NEW' AS PER BMPS-A8 APPENDIX B1
29 | Text Box | 1 | seongjin.lee | To facilitate IDD1 progress, the plot plan(IFR) is released with Code 2 on condition that CONTRACTOR ensures all the comments are incorporated into the IDD1.
30 | Callout | 1 | Joon Cho | Unit 005 Datum point ? SOC to confirm
31 | Callout | 1 | Robert.Kawitzki | Vertical ladders required. Max 15m between egress points