## 005-G-DAT-00005-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Julio.Aguilar | Ensure the use of the project finalized cover page for the all data sheets. | Noted. | Y
2 | Text Box | 1 | seongjin.lee | The document is approved as Code 2 subject to incorporation of information obtained during subsequent detailed engineering development. Prior to issue of the PO the datasheet shall include all the updated details and be in code 2 approval status. | Noted. | Y
3 | Cloud+ | 2 | Julio.Aguilar | Confirm this NPSHa value | NPSHa has been confirmed based on hydraulic calculation result. | Y
4 | Cloud+ | 2 | Julio.Aguilar | Confirm whether the pump autostart is required or manual start. | Manual start is confirmed and updated in Datasheet. | Y
5 | Callout | 2 | Julio.Aguilar | Final figures shall be updated when the final hydraulic calculation is finalized. | To be incorporated. | Y
6 | Callout | 2 | Julio.Aguilar | Remove prefix f | Removed. | Y
7 | Callout | 8 | Julio.Aguilar | Add: "Refer to project specification BMPS-S6 and BMPS-G2" | Added to note 9. | Y
8 | Cloud+ | 8 | Julio.Aguilar | Note 14 statement shall be consistent with NPSHa value. See further details Refer BMPS-G2 and BMPS-S6. | As per BMPS-G2 Para 8.3.4.3, NPSH margin will be considered. | Y