## 018-C-DAT-00020-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | rob.urban | These comments need to be addressed for all datasheets in the transmittal where applicable in the next revision and on the mechanical drawings
2 | Text Box | 1 | Mahdi Ali | THIS DATASHEET TEMPLATE WAS REVISED AND WILL BE ISSUED WITH THE HOMOGENIZATION PROCEDURE. IN THE NEXT REVISION, THE REVISED TEMPLATE AND COVER PAGE SHALL BE USED.
3 | Callout | 1 | Danut.Dragan | General Comments: 1. Level Instruments - the H or HH levels cannot coincide with the Max of any Level Range. Similarly for L or LL at Min Range. 2. Level Instruments Drawing - - Nozzles shall be marked on the drawing in as noted in the Nozzle Schedule (i.e. N5 A) - Correct number and Elevation / Orientation of Nozzles, relevant dimensions and angles shall be represented - The Liquid Level Limits: "LL", "L", "H", "HH" marks shall be followed by the Elevation figure relative to TTL. 3. Nozzle schedule: - nozzles for Level Instruments should be represented consistently: i.e. "N5 A" and "N5 B" or "N5 A-B" or "N5 A/B". - Service description shall be "Level Instrument" - Process Connection shall be as per the respective P&ID 4. Note 7 in this DS, or similar in all others: "The measuring range of all Level Measurement Instruments shall be the same." "... for the same service." shall be added
4 | Call-out | 5 | Rashed Almudahka | Add (as per BMPS-N1) to note no. 9.