## 018-C-DAT-00040-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 2 | Ahmed Bucheeri | As per EDP the spec for CS material is SA 516 GR70. To confirm
2 | Callout | 2 | Fatema Hashem | CHANGE THE NORMAL OPERATING PRESSURE TO 10-680 PSIG
3 | Callout | 2 | Fatema Hashem | CHANGE THE NORMAL OPERATING TEMPERATURE TO 100-445 F
4 | Callout | 3 | Danut.Dragan | add: "... for the same range."
5 | Call-out | 3 | Rashed Almudahka | As per BMPS-N1, P.P. insulation thickness shall be 50mm per mentioned asset operating temperature, please clarify
6 | Callout | 4 | Danut.Dragan | - All process connections to be tagged as in Nozzle Schedule, i.e. "N30(A)" - All Elevations to be checked and corrected if / where necessary - The Nuclear Detectors are not Intrusive, then there is no Nozzle attached. Process Connection as per Licensor d
7 | Callout | 4 | Danut.Dragan | add: "Density Transmitter"
8 | Callout | 4 | Danut.Dragan | add: "Level Switch"
9 | Callout | 4 | Danut.Dragan | add: "Level Transmitter"
10 | Callout | 4 | Danut.Dragan | add: "Level Transmitter"
11 | Callout | 4 | Danut.Dragan | Density Point Transmitter is not spanned
12 | Call-out | 4 | Rashed Almudahka | Note no. 15 referred in the sketch is incorrect. please clarify.
13 | Callout | 4 | Danut.Dragan | provide a clear reference: "ABOVE CONE-CYLINDER LINE"
14 | Callout | 4 | Danut.Dragan | shall read: "Nuclear Density and Level sources well"
15 | Callout | 5 | Danut.Dragan | add: "... NUCLEAR SOURCES FOR DENSITY & LEVEL INSTRUMENTS"
16 | Callout | 5 | Danut.Dragan | add: "Level Switch"
17 | Callout | 5 | Danut.Dragan | add: "Level Transmitter"
18 | Callout | 5 | Danut.Dragan | add: "Level Transmitter"
19 | Call-out | 5 | Rashed Almudahka | N3 nozzle size is shown as 3" in the P&ID. please clarify
20 | Call-out | 5 | Rashed Almudahka | N8 nozzle is not reflected in the P&ID. please clarify. Also, ensure nozzles consistency between GADs, PDS and respective P&ID
21 | Callout | 5 | Danut.Dragan | Nozzle tag - sequential Nos shall be different for the two different Instruments.
22 | Callout | 5 | Danut.Dragan | The level is measured through Density, but it is still a Level Instrument, as shown in P&ID (PV=Level in DCS). Avoid confusions with dedicated Density Instruments.