## 018-C-DAT-00046-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | AliRedha Malalla | Cover page is for train 2, however spec. sheet is for train 1. Please correct.
2 | Call-out | 3 | Rashed Almudahka | weld overlay to be marked
3 | Callout | 4 | Danut.Dragan | All nozzle heights shall be dimensioned (metric "mm", related to top / bottom tangent line) as per Instrumentation Specification
4 | Callout | 4 | Danut.Dragan | all respective nozzles marks shall be provided as noted in the Nozzle Schedule
5 | Callout | 5 | Danut.Dragan | Height / Position dimension (mm) - column shall be inserted in the table
6 | Callout | 5 | Danut.Dragan | in "Service" column should also be mentioned if the Instrument belongs to PCS or ESD. Also Instrument Tag can be added
7 | Callout | 5 | rob.urban | Not required here, only on mechanical datasheet/drawing