## 018-C-GAD-00002-003-R0
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Danut.Dragan | Location should be by a Thermo-Well - Bottom Head, as per the respective P&ID. Contractor to confirm and adjust accordingly.
2 | Callout | 1 | Danut.Dragan | Process Connection - Skin pad. Shall be clearly shown to avoid confusions.
3 | Callout | 1 | Danut.Dragan | Process Connections Symbol shall be different for: - Density Transmitter (bosses + supporting Pad) - Thermo-Couples, skin mounted. Mech Detailed Drawings might be mentioned.
4 | Callout | 1 | Danut.Dragan | SKIRT, as per the respective P&ID. Should read: Nozzle "65A/B". Contractor to confirm and adjust accordingly.