## 018-C-GAD-00020-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Danut.Dragan | Size of the Process Connection device / transmitter and supporting / reinforcement to be advised by Instrument Vendor
2 | Callout | 1 | Danut.Dragan | " ... DETECTOR's - SOURCE WELL" instead, for clarity
3 | Callout | 1 | Danut.Dragan | "DENSITY" shall read "LEVEL" as per CLG Instrument Tag.
4 | Callout | 1 | Danut.Dragan | "DETECTOR" should be replaced with "TRANSMITTER", unless the Vendor will use a Detector connected to a separate mounted Transmitter. Reason is, in P&ID they all are tagged as Transmitters, i.e. "AT", "LT"