## 018-G-DAT-00020-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | rob.urban | Comments to be discussed
2 | Text Box | 1 | Mahdi Ali | THIS DATASHEET TEMPLATE WAS REVISED AND WILL BE ISSUED WITH THE HOMOGENIZATION PROCEDURE. IN THE NEXT REVISION, THE REVISED TEMPLATE AND COVER PAGE SHALL BE USED.
3 | Text Box | 4 | Isamu | Check with Seal pump maker/seal vendor if impeller side mech seal flushing is covered by plan 53B. Otherwise provide suitable seal flush plan
4 | Text Box | 4 | Isamu | All seal flush and seal barrier liquid lines shall be SS piping as per FEED data sheet. Contractor is not at liberty to select softer option in case of conflict between various project documents. Correct and apply to all pumps
5 | Text Box | 5 | Isamu | All inspection and test specified as witnessed on FEED data sheet shall be remain witnessed. The use of the term Observed in the data sheet is rejected. Correct accordingly and put a remark as agreed on the definitions of words between API / BMPS and ITP,
6 | Callout | 7 | Fatema Hashem | Advise if catalyst fines/coke needs to be specified for short circulation pump operation
7 | Text Box | 7 | Isamu | High temperature service require also casing insulation to prevent :- 1. Personal injury 2. Thermal shock and casing cracking during rain or similar. 3. Fire hazard particularly with oil mist application, Refer to BMPS and and comply with,