## 018-G-DAT-00030-001-RB
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Ravi Kumar | OPEN COMMENT IN RESOLUTION SHEET OF REV A DATASHEET TO BE CLOSED
2 | Text Box | 1 | Mahdi Ali | THIS DATASHEET TEMPLATE WAS REVISED AND WILL BE ISSUED WITH THE HOMOGENIZATION PROCEDURE. IN THE NEXT REVISION, THE REVISED TEMPLATE AND COVER PAGE SHALL BE USED.
3 | Call-out | 2 | Ebrahim | Indicate method of starting the motor. Normally, Direct-On-Line (DOL)
4 | Callout | 2 | Mahdi Ali | INDICATE UNIT NO. AND THE FULL DESCRIPTION
5 | Call-out | 3 | Ali Hasan | The rational for 175 deg is not clear. Please review the discharge piping design temperture.
6 | Call-out | 4 | Ali Hasan | Refer to the comments on 018P0032A/B data sheet.
7 | Text Box | 6 | David.Jimenez | h
8 | Callout | 8 | Mahdi Ali | DO NOT QUOTE FEED NUMBER
9 | Text Box | 8 | Ali Hasan | The time for emptying out the sump to be included in the notes. Please add a note stating “The pump is designed to empty the sump in xxx minutes”.
10 | Call-out | 8 | Ali Hasan | The pump should be able to pump the maximum fluid temperature in the sump. There should be no limit on the maximum pumping temperature. Please modify.