## 018-L-PPN-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mohamed Aldoseri | 1RHCU SUBSTATION
2 | Call-out | 1 | Mohamed Aldoseri | 1RHCU substation layout drawing to be listed.
3 | Callout | 1 | Robert.Kawitzki | 80t crane is 3m wide. Provide access roads to accommodate - typical comment
4 | Callout | 1 | Robert.Kawitzki | Add paved turn radius
5 | Callout | 1 | Robert.Kawitzki | Add turn radius
6 | Text Box | 1 | Robert.Kawitzki | All areas inside the battery limit shall be paved
7 | Text Box | 1 | Robert.Kawitzki | All column shall be dimensioned as per BMPS A8 - typical comment
8 | Callout | 1 | Robert.Kawitzki | All text to be legible on an A3 print as per BMPS A8 5.5
9 | Callout | 1 | Robert.Kawitzki | All text, especially equipment tags shall be readable - typical comment
10 | Text Box | 1 | Robert.Kawitzki | Areas like these are very congested. Confirm where large bore control valves will be placed to ensure a vertical lift is possible - typical comment along all racks
11 | Callout | 1 | rob.urban | as per P&ID low points in piping between these exchangers shall be avoided or minimized By putting them all at grade low points are maximized
12 | Call-out | 1 | Mohamed Aldoseri | Assuming this is cables entry, Please refer the arrow in the legends. Also show all cable entries from/to the substation.
13 | Callout | 1 | Robert.Kawitzki | Bring filters to a lower level. Preferably ground level
14 | Callout | 1 | Robert.Kawitzki | C0004 and P0020B shall be close to F0002
15 | Call-out | 1 | Mahdi Ali | Change to 'A'
16 | Callout | 1 | Robert.Kawitzki | Column markers shall be provided and dimensioned as per BMPS A8
17 | Callout | 1 | Robert.Kawitzki | Confirm access to drop area
18 | Callout | 1 | Robert.Kawitzki | Confirm lift access to finfan
19 | Callout | 1 | Robert.Kawitzki | Confirm location of steamdrum placed within the clearance radius of the furnace
20 | Callout | 1 | Robert.Kawitzki | Confirm maintenance access to these pumps
21 | Callout | 1 | Robert.Kawitzki | Confirm minimum access area is provided for manhole access
22 | Callout | 1 | Robert.Kawitzki | Confirm that access space is available when piping is added - typical comment
23 | Callout | 1 | Robert.Kawitzki | Confirm that all ELs shown have taken HPP 5.000 into account
24 | Callout | 1 | Robert.Kawitzki | Confirm that no auto ignition pumps are placed on inside of the plot plan
25 | Callout | 1 | Robert.Kawitzki | Confirm truck turning radius
26 | Callout | 1 | Robert.Kawitzki | Confirm turn radius space is sufficient for the 80t crane. Refer BMPS A4 8.12.2 - typical comment
27 | Text Box | 1 | rob.urban | Consider moving
28 | Callout | 1 | rob.urban | Consider rotating 90 degrees and shorten pipe rack.
29 | Callout | 1 | Bernard.Grace | Corresponds
30 | Callout | 1 | Robert.Kawitzki | Discharge of pumps to be on a common centerline. Show the centerline - typical comment
31 | Callout | 1 | rob.urban | Distance should be 15 m min. as in other units
32 | Callout | 1 | Robert.Kawitzki | El TOS does not match elevation
33 | Text Box | 1 | Mohamed Aldoseri | Electrical
34 | Callout | 1 | Robert.Kawitzki | Elevation drawing to be added
35 | Text Box | 1 | Mohamed Aldoseri | Emergency
36 | Callout | 1 | Robert.Kawitzki | Ensure adequate access is provided for bundle removal - typical comment
37 | Callout | 1 | Robert.Kawitzki | Ensure bin storage area is optimized for bins and forklift for clear access between columns and foundations
38 | Callout | 1 | Robert.Kawitzki | Ensure minimum access space is provided around equipment as per project requirements - typical comment
39 | Callout | 1 | Robert.Kawitzki | Ensure that all staircases are as per project requirements - typical comment
40 | Callout | 1 | Robert.Kawitzki | Ensure that cantilevered platform does not impede bundle removal on ground floor
41 | Callout | 1 | Robert.Kawitzki | Ensure that minimum clearances are provided around equipment in and under structures including piping, pipe supports, valve operators, instruments, utility stations etc - typical comment
42 | Callout | 1 | Robert.Kawitzki | Ensure that steelwork is provided to allow NB50 pipe to span - typical comment
43 | Callout | 1 | Robert.Kawitzki | Ensure there is no gravel in front of emergency generator access
44 | Callout | 1 | rob.urban | Extra space required for steam turbine piping
45 | Callout | 1 | rob.urban | Extra space required for steam turbine piping
46 | Text Box | 1 | Ali Hasan | General comment: the storage area for oil and chemical to be allocated and reflected in the plot plan. The area shall have a raised concrete paving and accordance to the project specification. Refer to ITB Vol 2, SECTION 6/SUB-SECTION 6.3.3-CIVIL-page 3/6 in which details of the storage area is provided.
47 | Callout | 1 | Robert.Kawitzki | if these are ramps then show correctly
48 | Callout | 1 | rob.urban | IS THIS SPACE FOR EB PUMP ACCESS AND REMOVAL?
49 | Callout | 1 | Robert.Kawitzki | Laydown not letdown - typical comment
50 | Callout | 1 | rob.urban | LETDOWN STATIONS COULD EASILY NEED 11 M X 5 M SPACE
51 | Callout | 1 | Robert.Kawitzki | Lift study required to ensure that ALL finfans are accessible by crane
52 | Callout | 1 | Robert.Kawitzki | Maintenance access roads to have paved turn in radius. These are NOT one way streets. Minimum width shall be 4000mm - typical comment
53 | Call-out | 1 | Mahdi Ali | Material Class for plot plans is not 'L'. Change to 'A'
54 | Callout | 1 | Robert.Kawitzki | Move E0019 on to NS rack close to C003 and P0012AB
55 | Callout | 1 | Robert.Kawitzki | Move P0002AB closer to V0007
56 | Callout | 1 | Robert.Kawitzki | Move P0015AB and C0005 to west end of this rack to be closer to C0003
57 | Callout | 1 | Bernard.Grace | No letter to prefix unit number
58 | Callout | 1 | Bernard.Grace | No letter to prefix unit number
59 | Call-out | 1 | Mahdi Ali | Not as per BMPS-A8
60 | Text Box | 1 | Ahmed Habib | Paved area required as a car park for Rack room visitors such as (Maintenance, Process Control Engineers, Operators, Inst. Engineers, etc. )
61 | Text Box | 1 | rob.urban | PLEASE ORGANIZE A MEETING WHERE WE CAN DISCUSS AND CLARIFY ALL COMMENTS
62 | Callout | 1 | Robert.Kawitzki | Provide 6m wide access next to rack
63 | Callout | 1 | Robert.Kawitzki | Provide paved turn radius
64 | Text Box | 1 | Sankara | Refer to Note 2 on FEED Sub station Layout. Ensure that adequate space has been allocated for the substation, to facilitate safe operation, future extension and maintainability.
65 | Callout | 1 | Robert.Kawitzki | Relocate analyzer house close to rack
66 | Callout | 1 | Robert.Kawitzki | Relocate closer to C0001
67 | Callout | 1 | rob.urban | Relocate these exchangers (platform above E0005) They receive very hot feed from V1004 and V2004 and very fouling service. Free drain into E0005
68 | Callout | 1 | Robert.Kawitzki | Requires double door for equipment - typical comment where applicable
69 | Callout | 1 | Robert.Kawitzki | Rotate hoppers and structure 90 degrees and move associated equipment to suit. Move EW rack one bay south to allow more room for equipment north of the rack. Move equipment south of rack to suit.
70 | Call-out | 1 | Mohamed Aldoseri | Second Door is required
71 | Call-out | 1 | Mohamed Aldoseri | Second door location to be reconsidered to be on the north side of the substation depends on the equipment layout in the HVAC room
72 | Callout | 1 | Robert.Kawitzki | Secondary egress ladders to be shown - typical all structures
73 | Callout | 1 | Robert.Kawitzki | Section arrow incorrectly placed
74 | Text Box | 1 | Robert.Kawitzki | Show column markers (A & 1) - typical comment
75 | Callout | 1 | Robert.Kawitzki | Show crane parking area for PSV removal - typical comment all PSV platforms
76 | Callout | 1 | Robert.Kawitzki | Show HP EL for all roads
77 | Callout | 1 | Robert.Kawitzki | Show minimum clearance radius dimension
78 | Callout | 1 | Robert.Kawitzki | Show plot limit in correct location
79 | Callout | 1 | Robert.Kawitzki | Show ramps correctly
80 | Callout | 1 | Robert.Kawitzki | Show section direction changes - typical comment where required
81 | Callout | 1 | Robert.Kawitzki | Show size of area - typical comment all letdown areas
82 | Callout | 1 | Robert.Kawitzki | Show the outline as a building. This is a compressor house with walls
83 | Callout | 1 | Robert.Kawitzki | Show TOS for walkway; be consistant
84 | Callout | 1 | Bernard.Grace | Substation No: lSST018R01
85 | Callout | 1 | Robert.Kawitzki | Swap B018STR200 with compressor unit to optimize pipe runs from exchangers to columns
86 | Callout | 1 | Robert.Kawitzki | Swap P0013AB with P0016AB and P0014AB to optimize piping. P0016AB are auto ignition and shall be closer to C0003
87 | Callout | 1 | Robert.Kawitzki | Take into consideration area required for ebullating pumps VFDs/transformers. Basis discussion with Flowserve. Preliminary substation equipment layout shall be provided at the earliest to verify size of SS including 30% future allowance In light of this I would suggest moving the SS north to where the rack room is and move the rack room south to the current SS location
88 | Callout | 1 | Robert.Kawitzki | Take paving right up to the substation all around
89 | Text Box | 1 | Robert.Kawitzki | The fractionator pumparound loop to be reviewed. Equipment locations can be optimized to minimize piperun lengths
90 | Callout | 1 | Sankara | There are two Emergency Diesel Generators
91 | Callout | 1 | Robert.Kawitzki | This equipment must be optimized according to process flow to minimize pipe runs. Also free draining between E1005 to E1006 to V1006- typical comment both trains
92 | Callout | 1 | Robert.Kawitzki | This is a process rack in the elevation. Show column alignment bubbles for all structures and dimension all column lines - typical comment all structures
93 | Callout | 1 | Robert.Kawitzki | This is the unit limit
94 | Call-out | 1 | Mohamed Aldoseri | This is to be paved area
95 | Callout | 1 | Robert.Kawitzki | Use font as per legend
96 | Text Box | 1 | Sankara | Use the right tag number and name for substation.
97 | Callout | 1 | Bernard.Grace | What is not shown?
98 | Call-out | 1 | Mohamed Aldoseri | What is the Road dimension?
99 | Callout | 1 | Robert.Kawitzki | What is the width of the access road? 80t crane is 3m wide so minimum shall be 4m. Confirm - typical all access roads
100 | Callout | 1 | Robert.Kawitzki | What is this? Each transformer requires individual gate with separate manway access
101 | Text Box | 1 | Robert.Kawitzki | Where is the crane parking area for PSV maintenance removal? - typical comment for all PSV platforms
102 | Text Box | 1 | Robert.Kawitzki | Why is this drawing squeezed in at this ridiculous scale? Show sections on separate drawing. If need be, split the plot plan