## 018-S-GAD-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | 62756
2 | Call-out | 1 | Ebrahim | Add the electrical main cable routing layout as it has direct impact on this drawing
3 | Callout | 1 | Robert.Kawitzki | All text must be legible
4 | Call-out | 1 | Ali Abbas | Analyser house and associated HVAC in-take stack no reflected in the plot.
5 | Call-out | 1 | Mohamed Aldoseri | As the whole area is paved, provide sectional diagram showing concrete wall intsallation where the electrical and instrument cables routing are crossing each other - Typical
6 | Call-out | 1 | Ali Abbas | Cables access to SRR to be from underground pits through transit blocks
7 | Call-out | 1 | Ebrahim | Call as: GENERAL UNDER GROUND SERVICES NO.1 RESIDUE HYDROCRACKING UNIT
8 | Text Box | 1 | Chandrahasan D | Clarify this whether drawing is a composite u/g utilities drawing. If yes, outline of equipment foundations to be shown to see their interference with routing. Paving and slope details to be shown in separate drawing (OR ) in light line weights. There is no consistency between the operating centers in the drawing presentation.
9 | Call-out | 1 | Ebrahim | CONCRETE COVER (WITH RED COLOURED TOPPING)
10 | Call-out | 1 | Ali Abbas | difficult to differentiate between elec and inst
11 | Callout | 1 | Chandrahasan D | Drawing title to conform to BMPS-A8 section 6.3.2 requirement
12 | Text Box | 1 | Mohamed Aldoseri | Electrical cable numbers of entries/deimensions to be updated after finalizing the total number of outgoing cables
13 | Text Box | 1 | Mohamed Aldoseri | Electrical substation shall be updated as per final layout
14 | Text Box | 1 | Mahdi Ali | EN0815
15 | Call-out | 1 | Ali Abbas | Ensure concrete duct for inst cables is used for all areas of heavy vehicle access
16 | Callout | 1 | Chandrahasan D | EPC contractor to preppare their Own Standard drawing??
17 | Text Box | 1 | Ahmed Habib | General Comment: After finlizing the I/Os of instrumentation and all type of communcation connection such as Process and corporate Network, CCTV, FOs, Telephone, etc.. , it shall be reflected in the second version of the drawing.
18 | Text Box | 1 | Omran A | General Comment: 1-SRR size to be finalized during details design (once total No of Control Systems are identified/finalized) 2- Parking slots to be allocated. 3- Double sealed door for hardware/equipment access to be relocated towards North side away from plant, (high-up track access). 4- Air-lock doors to be introduced as per BMPS-R1 Paragraph 6.3.7. 5- SRR to be in-line with BMPS-R1 and BMPS-R2.
19 | Call-out | 1 | Mohamed Aldoseri | Generator room is not applicable, revise as per latest building layout.
20 | Dimension | 1 | Ebrahim | H
21 | Call-out | 1 | Ebrahim | HATCHING NOT MATCHING WITH LEGEND
22 | Text Box | 1 | Omran A | Identify Room Service
23 | Call-out | 1 | Ebrahim | IN PAVED AREA
24 | Callout | 1 | Mahdi Ali | INCLUDE UNIT DESCRIPTION
25 | Call-out | 1 | Ebrahim | IS CONCRETE WALL IS REQUIRED AT THIS AREA?
26 | Callout | 1 | Chandrahasan D | Manholes and catch basins to have unique numbering
27 | Call-out | 1 | Ebrahim | OVERLAP BETWEEN ELEC. & INST. TRENCHES NEED TO BE ADDRESSED PROPERLY. AT PAVED AREAS TYPICAL
28 | Call-out | 1 | Ebrahim | PASSING THROUGH FUTURE AREA NEED TO BE AVOIDED. Typical
29 | Text Box | 1 | AliRedha Malalla | Please ensure no u/g pipe pasess below foundations.
30 | Text Box | 1 | Bader Abdulrahman | Refrence to type of the material used for pipe services?
31 | Text Box | 1 | Robert.Kawitzki | Show sections in busy areas to prove that this is actually doable
32 | Call-out | 1 | Ali Abbas | Size to be finalized once I/O counts including package units are identifed
33 | Call-out | 1 | Ali Abbas | State Satellite Rack Room or SRR as agreed with assigned unit no.
34 | Call-out | 1 | Ebrahim | SUBSTATION LAYOUT IS NOT MATCHING WITH U018 GENERAL PLOT PLAN
35 | Callout | 1 | Chandrahasan D | Suggested to common legend and abbreviations drawing for all operating centers
36 | Call-out | 1 | Ebrahim | TELEPHONE AND LAN ARE MISSING
37 | Text Box | 1 | Mahdi Ali | USE LATEST BORDER THAT IS PART OF THE HOMOGENIZATION PROCEDURE.
38 | Callout | 1 | Robert.Kawitzki | Verify size of the substation
39 | Callout | 1 | Robert.Kawitzki | Verify that ug pipes do not clash with civil - typ comment
40 | Dimension | 1 | Ebrahim | W
41 | Call-out | 1 | Ali Abbas | What about GAS Monitor? Both F&G needs to be reflected for consistency. Needs to be reviewed and finalised by loss prevention.