## 021-L-PPN-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Robert.Kawitzki | 021U0002 not shown
2 | Text Box | 1 | Hasan Asad | 1. Lubricants and chemical storage location(s) shall be sheltered with easy access for material delivery. 2. Overhead cranes shall be designed to reach ground level for material delivery. 3. Packages equipment accessibility shall be reviewed once information is available. Preferable to have Hiab direct access for rigging jobs.
3 |  | 1 | AutoCAD SHX Text | 29° 47' 37"
4 | Call-out | 1 | Mohamed Aldoseri | 3HDU SUBSTATION
5 | Text Box | 1 | Hasan Asad | Additional laydown area to set here.
6 | Callout | 1 | Robert.Kawitzki | Air coolers at EL21.600 or 25.000?
7 | Callout | 1 | Robert.Kawitzki | Analyzer house
8 | Callout | 1 | Bernard.Grace | and maintenance Team
9 | Text Box | 1 | fradicchi | C
10 | Text Box | 1 | Robert.Kawitzki | C021PR100
11 | Call-out | 1 | Ebrahim | Car park is essential to serve S/S and SSR maintenance, P&U and Process Control Engineers
12 | Call-out | 1 | Hasan Al Noaimi | catalyst area to be asphalted or cemented Not cravel as per our discussion.
13 | Call-out | 1 | MAK | Change L to A which is the correct Material Class for Plot Plan.
14 | Call-out | 1 | MAK | Change to Upper Case
15 | Callout | 1 | rob.urban | COMMENTS NEED TO BE DISCUSSED IF AGREED AT THE BEGINNING OF 3D MODELLING
16 | Callout | 1 | Robert.Kawitzki | Confirm access to pumps/motors for maintenance - typical comment for all pumps between structures
17 | Callout | 1 | Robert.Kawitzki | Confirm adequate room is provided between exchangers including piping, valve operators, instruments, pipe supports etc - typical comment
18 | Callout | 1 | Robert.Kawitzki | Confirm adequate room is provided between pumps incl piping - typical comment
19 | Callout | 1 | Robert.Kawitzki | Confirm sufficient entry access points are provided (30m rule)
20 | Callout | 1 | Robert.Kawitzki | Confirm that adequate maintenance access room is provided around vessels in structures with all piping, instruments, pipe supports, utility stations etc in place - typ comment all structures
21 | Callout | 1 | Robert.Kawitzki | Confirm that none of the pumps in this unit require curbing. If so, show it
22 | Call-out | 1 | MAK | Delete C and never use prefixes for Unit Nos.
23 | Call-out | 1 | MAK | Delete HDU- and HRU-
24 | Callout | 1 | Robert.Kawitzki | Ensure sufficient space is provided including piping, valve operators, pipe supports, instruments, utility stations etc - typical comment for all structures
25 | Callout | 1 | Bernard.Grace | Ensure there is sufficient space to permit removal and replacement of equipment as required during operation of plant
26 | Callout | 1 | Bernard.Grace | Ensure this area is accessible by vehicle for delivery and removal of 200L drums
27 | Callout | 1 | Robert.Kawitzki | Equipment list shall be alphabetically ordered
28 | Text Box | 1 | Ahmed Habib | General Comment for All SRR: Paved car parking area shall be provided to serve the Satellite Rack room visitors
29 | Text Box | 1 | rob.urban | GENERAL COMMENT: HAS THE PROCESS FLOW BEEN FOLLOWED SO EQUIPMENT IS LOCATED SUCH THAT PIPE RUNS ARE MINIMIZED
30 | Callout | 1 | Bernard.Grace | Include the nearest Survey Control Stations/Monuments to aid setting out and construction within the plot plan
31 | Callout | 1 | Robert.Kawitzki | Maintenance access to be sufficient with paved access radius provided - typ comment
32 | Call-out | 1 | Mahdi Ali | Material class for plot plans is 'A' and not 'L'
33 | Text Box | 1 | Robert.Kawitzki | Move
34 | Call-out | 1 | Ebrahim | Normal practice, all the areas around the substation are paved.
35 |  | 1 | AutoCAD SHX Text | NORTH
36 |  | 1 | AutoCAD SHX Text | NORTH
37 | Text Box | 1 | Robert.Kawitzki | Note 1
38 | Text Box | 1 | Robert.Kawitzki | Note 1
39 | Text Box | 1 | Robert.Kawitzki | Note 1: Optimize 4 off exchangers to process flow requirements
40 | Callout | 1 | Robert.Kawitzki | Optimize; consider stacking
41 | Text Box | 1 | Ravi Kumar | PREPARE AND SUBMIT FORMALLY A CONSOLIDATED LIST OF MAJOR CHANGES AND THE BASIS FOR CHANGE FROM FEED PLOT PLAN TO IBD ISSUE FOR OFFICIAL RECORDS PURPOSE
42 |  | 1 | AutoCAD SHX Text | PREVALING
43 | Callout | 1 | Robert.Kawitzki | Provide column marker numbers/alphas for all structures - typical comment
44 | Callout | 1 | Robert.Kawitzki | Provide eastings for roads
45 | Callout | 1 | Robert.Kawitzki | Provide paved turn radius. Traffic goes both directions. Typical comment
46 | Call-out | 1 | Mohamed Aldoseri | Provide Paving in this area
47 | Dimension | 1 | Ebrahim | Provide wider maintenance access which could be also utilized for car parking
48 | Callout | 1 | Robert.Kawitzki | PSA unit Adsorbant
49 |  | 1 | AutoCAD SHX Text | R=15240
50 |  | 1 | AutoCAD SHX Text | R=15240
51 |  | 1 | AutoCAD SHX Text | R=22860
52 |  | 1 | AutoCAD SHX Text | R=7620
53 | Callout | 1 | Robert.Kawitzki | Rack Room location and design to be confirmed
54 |  | 1 | AutoCAD SHX Text | REFINERY
55 | Call-out | 1 | Mahdi Ali | Remove letter 'C'
56 | Callout | 1 | Robert.Kawitzki | Secondary escape ladders to be shown to confirm exit paths and max height of 6000mm - typical comment
57 | Text Box | 1 | Robert.Kawitzki | Show all column line markers and dimension as per BMPS A8
58 | Text Box | 1 | Robert.Kawitzki | Show at larger scale, this is useless on a A3
59 | Callout | 1 | Robert.Kawitzki | Show column nominators - typical comment
60 | Text Box | 1 | Robert.Kawitzki | Show elevation through plant to show height of all vessels
61 | Text Box | 1 | Robert.Kawitzki | Show elevations for C021SLT100, C021SLT200 and C023SLT200
62 | Callout | 1 | Robert.Kawitzki | Show elevations to see overall height of structure - typical comment
63 | Callout | 1 | Robert.Kawitzki | Show hatching away from text
64 | Callout | 1 | Robert.Kawitzki | Swap Amine and water injection equipment location with compressor equipment location to optimize and minimize piping
65 | Callout | 1 | Robert.Kawitzki | Tail Gas line from V0014 to F0001 will be too long with low pressure
66 | Callout | 1 | Robert.Kawitzki | Text height to be as per BMPS A8 with no exceptions
67 | Callout | 1 | Robert.Kawitzki | Text is too small. Drawing will be rejected as per BMPS A8
68 | Text Box | 1 | Hasan Asad | The laydown areas shall have clear access to fetch equipment components using Hiab or forklift. It is prefered that overhead crane access is granted to the laydown areas as well.
69 |  | 1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not. under any circumstances. be totally or partially. directly or indirectly. transferred. reproduced. copied. disclosed or used. without its prior written consent. for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
70 | Callout | 1 | Robert.Kawitzki | These roads do not look like they are wide enough. A 80t crane is 3m wide. Provide a minimum 4m wide access fit for purpose - typ comment
71 | Callout | 1 | Robert.Kawitzki | TOS tiers do not match. Typ all tiers
72 |  | 1 | AutoCAD SHX Text | TRUE
73 | Call-out | 1 | Ali Kadhem | TTSJV to ensure that the area is adequate for both the spent and fresh catalyst. The empty UN approved 200L drums and pallets required for spent catalyst unloading are shifted in advance from Bapco stores to the plant. The fresh catalyst is also laid out in advance in the plant as per a catalyst layout plan prepared for each catalyst system. For more details about Bapco’s requirements for the catalyst unloading and loading area, refer to Bapco’s comments on the MoM of the 3HDU/1HRU Plot Plan review meeting in the mail dated 10 May 2018. Please review and revise accordingly.
74 | Call-out | 1 | Ali Kadhem | TTSJV to ensure that the area is adequate for both the spent and fresh catalyst. The empty UN approved 200L drums and pallets required for spent catalyst unloading are shifted in advance from Bapco stores to the plant. The fresh catalyst is also laid out in advance in the plant as per a catalyst layout plan prepared for each catalyst system. Most of the fresh catalyst is supplied in bags and cannot be put in two levels. Based on preliminary calculation, the area of 480m2 is not adequate and much less than the required area. For more details about Bapco’s requirements for the catalyst unloading and loading area, refer to Bapco’s comments on the MoM of the 3HDU/1HRU Plot Plan review meeting in the mail dated 10 May 2018. Therefore, the area of 480m2 is not acceptable and please review and revise accordingly.
75 | Callout | 1 | Robert.Kawitzki | What height is this walkway?
76 | Callout | 1 | Robert.Kawitzki | What is the distance between C021PR200 and C021PR100? Conform to max allowable pipe spans - typical comment for all interconnecting piope
77 | Callout | 1 | Robert.Kawitzki | Which equipment is H0002?
78 | Callout | 1 | Robert.Kawitzki | Why is this process tier shown as side steel?
79 | Call-out | 1 | MAK | Why Owner Disclaimer Note is different? Please use the latest border that is part of the Homogenisation Procedure which has the official Disclaimer Note.
80 |  | 1 | AutoCAD SHX Text | WIND