## 021-L-PPN-00002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Mohamed Aldoseri | 3 HDU Substation
2 | Call-out | 1 | Mohamed Aldoseri | all areas around the substation shall be paved
3 | Call-out | 1 | Hasan Al Noaimi | All catalyst areas to be paved with concorate.
4 | Text Box | 1 | Mohamed Aldoseri | Cable enteries to electrical substation to be shown in this drawing
5 | Callout | 1 | Robert.Kawitzki | Define and/or show detail for piping interface with main rack model. Will it be a straight cut at N1855.250 or to the nearest weld at a fitting?
6 | Text Box | 1 | Mohamed Aldoseri | Electrical
7 | Call-out | 1 | Mohamed Aldoseri | Individual gate with seperate manways for each transformer, applicable to all transformers bay.
8 | Callout | 1 | Robert.Kawitzki | Is this correct? Are you planning to go to the centerline of the road off the unit parameters?
9 | Text Box | 1 | Ahmed Habib | Maintenance Access
10 | Call-out | 1 | Mahdi Ali | Material Class for Plot plans is 'A' and not 'L'
11 | Call-out | 1 | Mahdi Ali | Material Class for Plot plans is 'A' and not 'L'
12 | Call-out | 1 | Mahdi Ali | Material Class for Plot plans is 'A' and not 'L'
13 | Call-out | 1 | Mahdi Ali | Material Class for Plot plans is 'A' and not 'L'
14 | Call-out | 1 | Mahdi Ali | Material Class for Plot plans is 'A' and not 'L'
15 | Call-out | 1 | Mahdi Ali | Material Class for Plot plans is 'A' and not 'L'
16 | Call-out | 1 | Hasan Al Noaimi | No cravel in catalyst area.
17 | Text Box | 1 | Ahmed Habib | Paved area shall be provided as a car park to serve the SRR visitors (Instrument Maintenance, Automation and Instrument Engineers, operators, etc..
18 | Call-out | 1 | Mahdi Ali | Remove letter 'C' in front of the unit numbers.
19 | Callout | 1 | Robert.Kawitzki | Show design segregation for lines leaving the rack
20 | Callout | 1 | Robert.Kawitzki | SS structure shown in zone C? Add note to that effect - typical comment
21 | Callout | 1 | Robert.Kawitzki | This drawing is for design zone limits. Use the correct font to denote as such
22 | Call-out | 1 | Hasan Al Noaimi | to be sheltered.
23 | Call-out | 1 | Ali Kadhem | TTSJV to ensure that the area is adequate for both the spent and fresh catalyst. The empty UN approved 200L drums and pallets required for spent catalyst unloading are shifted in advance from Bapco stores to the plant. The fresh catalyst is also laid out in advance in the plant as per a catalyst layout plan prepared for each catalyst system. For more details about Bapco’s requirements for the catalyst unloading and loading area, refer to Bapco’s comments on the MoM of the 3HDU/1HRU Plot Plan review meeting in the mail dated 10 May 2018. Please review and revise accordingly.
24 | Call-out | 1 | Ali Kadhem | TTSJV to ensure that the area is adequate for both the spent and fresh catalyst. The empty UN approved 200L drums and pallets required for spent catalyst unloading are shifted in advance from Bapco stores to the plant. The fresh catalyst is also laid out in advance in the plant as per a catalyst layout plan prepared for each catalyst system. Most of the fresh catalyst is supplied in bags and cannot be put in two levels. Based on preliminary calculation, the area of 480m2 is not adequate and much less than the required area. For more details about Bapco’s requirements for the catalyst unloading and loading area, refer to Bapco’s comments on the MoM of the 3HDU/1HRU Plot Plan review meeting in the mail dated 10 May 2018. Therefore, the area of 480m2 is not acceptable and please review and revise accordingly.
25 | Callout | 1 | Robert.Kawitzki | Use correct font - typical comment
26 | Call-out | 1 | Mohamed Aldoseri | What is the dimension of the maintenance access road? adequate space is required for trucks