## 023-L-INX-00002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | Why the cover sheet is A3 size and the rest of the spreadsheet is A4 size? Use the correct cover sheet size. The latest templates include the correct cover sheets.
2 | Call-out | 2 | Ali Kadhem | TTSJV to confirm that all the spare coolers/compressor intercoolers are included in cooling water balance, as per the Technical Query T251. Additionally, to confirm that the new PSA Inlet Cooler 023E0004 added during EPC, as per the Technical Query T1972 is also included in the revised cooling water balance.
3 | Text Box | 2 | Ali Kadhem | TTSJV to confirm that the process data are based on the latest revised H&MB of 1HRU, because we do not have yet the latest revised H&MB for 1HRU.
4 | Call-out | 2 | Ali Kadhem | With reference to IBD issue of the 1HRU P&ID (023-A-PID-00005-001), P-0071 (8” size) is the “SWEET OFF-GAS TO FUEL GAS SYSTEM” line. Please refer also to note no.9 on the same sheet. Please check and revise the data.