## 050-A-PID-00001-001-R8A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | A Albalooshi | Please provide the description of the service.
2 | Callout | 1 | Abdul Rahim | why this is hashed
3 | Callout | 1 | Abdul Rahim | AB 4 Crude pipeline from Saudi
4 | Callout | 1 | Abdul Rahim | Why Rvs setting at 100 psig. Line normal pressure is approx 100 psig. Confirm
5 | Callout | 1 | Abdul Rahim | Add: /
6 | Call-out | 1 | Edgardo | Please confirm the routing of the discharge of these relief valves
7 | Call-out | 1 | Edgardo | Please change to BMPS-L-144014
8 | Call-out | 1 | Edgardo | Please delete arrow head; flow is bi-directional
9 | Call-out | 1 | Edgardo | Most of the new BMP lines in this 050 PID are not provided yet with required vents and drains. Need to ensure that this requirement is not missed during project execution. Similar to the other Offsite areas, please consider 1 1/2" size for drains since most of the lines are long. The bigger sized drains will allow shorter time for draining, where required, as well as facilitate connection of hose if required for draining. This comment applies to all PIDs in Unit 050
10 | Call-out | 1 | Edgardo | Please use the new format of the drawing number; please confirm also the location of the interface point, as these tanks are within the scope of MOC
11 | Call-out | 1 | Edgardo | With the potential that the implementation of this general note may be missed, it is suggested to put a Hold item on those lines where thermal relief valves may be potentially required. This HOLD could serve as a reminder; this comment applies to all PIDs in this Unit 050
12 | Call-out | 1 | Edgardo | Please consider revising Note 4, as follows: The tie-in schedule shall be agreed with Owner, taking into consideration various factors, such as the BMP commissioning / start up requirements
13 | Call-out | 1 | Edgardo | These line breaks are very long and are quite difficult to know the connection of the lines
14 | Call-out | 1 | Edgardo | The availability of these stubs for tie-ins shall be confirmed during site survey; Refer also to comment on Note 6
15 | Call-out | 1 | Edgardo | Please revise this Note 6, considering that the AB4 pipeline commissioning is expected this year and hence, the assumption for scheduling the tie-in will not be valid
16 | Callout | 1 | Francis L | Change to FIT
17 | Callout | 1 | Mahdi Ali | A3
18 | Callout | 1 | Mahdi Ali | THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER AS NEXT REVISION. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS
19 | Callout | 1 | Mahdi Ali | BAPCO PROVIDED THIS DRAWING AS REVISION '7'. THUS THIS DRAWING SHALL BE '7A'
20 | Typewritten Text | 1 | Nabeel | Add 050D0164
21 | Typewritten Text | 1 | Nabeel | Add "(AB4)"
22 | Typewritten Text | 1 | Nabeel | write the service of the tanks "Bahrain/Rubble Crude Tanks"