## 050-A-PID-00001-003-R8A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | A Albalooshi | Please indicate valve size
2 | Callout | 1 | A Albalooshi | Please indicate valve size
3 | Callout | 1 | Abdul Rahim | Location of spill back valves to tanks needs to be located in one area, easy for operators to switch valves from one place
4 | Callout | 1 | Abdul Rahim | Valve is needed. This tie in can be done during 4A T&I
5 | Call-out | 1 | Edgardo | Please change to 1 1/2" the size of drain valves; drain valve to be installed at bottom of flange, same more or less as the bottom of pipe ID
6 | Callout | 1 | Mahdi Ali | BAPCO PROVIDED THIS DRAWING AS REVISION '7'. THUS THIS DRAWING SHALL BE '7A'
7 | Callout | 1 | Mahdi Ali | THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER AS NEXT REVISION. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS