## 050-A-PID-00002-007-R6A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | change to 3/4"
2 | Call-out | 1 | Edgardo | Please confirm the use of globe valve. in current pipe spec C9M, globe valve is not included
3 | Callout | 1 | Francis L | Indicate as SP here, against the relevant signal.
4 | Callout | 1 | Francis L | Clarify function of this seq block and indicate as a NOTE on this dwg.
5 | Callout | 1 | Francis L | Indicate RATIO here
6 | Callout | 1 | Francis L | Existing instrumentation system is conventional analog. Hence, use conventional analog instead of FF for Ref Tank Farm. Applies to whole of Ref Tank Farm.
7 | Callout | 1 | Francis L | FE tag need not be indicated on P&ID. Refer to BMPS-A-50003.
8 | Callout | 1 | Francis L | Clarify whether this should be an ESD valve. Consider bypass for it.
9 | Callout | 1 | Francis L | Clarify whether two separate DCS AIs (RVP & TVP) are required.
10 | Callout | 1 | Mahdi Ali | THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER AS NEXT REVISION. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS
11 | Callout | 1 | Mahdi Ali | BAPCO PROVIDED THIS DRAWING AS REVISION '5'. THUS THIS DRAWING SHALL BE '5A'