## 050-A-PID-00005-001-R6A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Edgardo | Please reverse the direction of the arrow head; the flow is to the tank
2 | Typewritten Text | 1 | Nabeel | Add Tank Service Descriptions
3 | Call-out | 1 | Edgardo | This should be 24" instead of 26"; Please note that if the tank can be shutdown and new permanent inlet nozzles will be installed, the use of inlet diffuser to reduce the inlet velocity shall be considered, in lieu of enlarged inlet pipe which require bigger sized valves
4 | Call-out | 1 | Edgardo | This line break is long and is difficult to identify the connection; please improve the presentation
5 | Callout | 1 | Mahdi Ali | BAPCO PROVIDED THIS DRAWING AS REVISION '5'. THUS THIS DRAWING SHALL BE '5A'
6 | Call-out | 1 | Edgardo | Please show Note 7 for this diffuser
7 | Callout | 1 | Mahdi Ali | THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER AS NEXT REVISION. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS
8 | Callout | 1 | Abdul Rahim | change to 1 1/2"
9 | Call-out | 1 | Edgardo | This line break is long and is difficult to identify the connection; please improve the presentation