## 050-A-PID-00006-001-R5A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | Clarify whether the 2 conditions are either OR.
2 | Callout | 1 | Francis L | Tag is not shown. Refer to BMPS-A-50003. Applies to other similar tags.
3 | Callout | 1 | Mahdi Ali | BAPCO PROVIDED THIS DRAWING AS REVISION '4'. THUS THIS DRAWING SHALL BE '4A'
4 | Call-out | 1 | Edgardo | This spectacle blind may need to be at close position during normal operation, to ensure positive isolation;
5 | Callout | 1 | Francis L | Include the tag numbers of the 3 MOVs in this note.
6 | Call-out | 1 | Edgardo | Please clarify the requirement for the new gooseneck vent, considering that tank is provided with nitrogen blanket; the availability of existing breather valves / vents / roof nozzles shall be verified during site survey; This comment applies to all tanks where new goosneck vents are being provided
7 | Call-out | 1 | Edgardo | This requirement to be reviewed and clarified if applicable for Offsite areas; this comment applies to relevant PIDs in Unit 050
8 | Text Box | 1 | Francis L | Clarify absence of tag sequential numbers and MOV tagging.
9 | Typewritten Text | 1 | Nabeel | Add high point vent
10 | Callout | 1 | Francis L | valves
11 | Call-out | 1 | Edgardo | This line break is long and not easy to know the connection; please improve the presentation of the line
12 | Callout | 1 | Abdul Rahim | 3 HDU and 2 HDU need to to routed separately to the MFD. each unit when starts up its rundown will be routed to its feed tank, until diesel is on spec then will be routed to 10 ppm MFD
13 | Call-out | 1 | Edgardo | Please confirm this line, which is shown inside the cloud. This is an existing line; See Note 3; Need to be verified during the site survey
14 | Call-out | 1 | Edgardo | Please consider minimum length for this line; there is normally no flow in this line and will be a dead leg
15 | Callout | 1 | Francis L | Indicate action
16 | Callout | 1 | Mahdi Ali | THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER AS NEXT REVISION. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS