## 050-A-PID-00006-002-R5A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Edgardo | The line breaks are long and not easy to identify the connections; please improve the presentation
2 | Typewritten Text | 1 | Nabeel | Tank Services
3 | Call-out | 1 | Edgardo | New inlet line shall be provided with 4" stub with valve and blind to facilitate the initial filling of the tank
4 | Callout | 1 | Mahdi Ali | BAPCO PROVIDED THIS DRAWING AS REVISION '4'. THUS THIS DRAWING SHALL BE '4A'
5 | Callout | 1 | Abdul Rahim | Two separate lines need to be routed to 10 ppm DSL MFD. 3HDU during start up DSL rundown will be routed to its feed tank until DSL is on spec
6 | Callout | 1 | Mahdi Ali | THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER AS NEXT REVISION. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS
7 | Text Box | 1 | Omran A | Asset No missing?