## 050-A-PID-00008-001-R5A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Mahdi Ali | THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER AS NEXT REVISION. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS
2 | Callout | 1 | Mahdi Ali | BAPCO PROVIDED THIS DRAWING AS REVISION '4'. THUS THIS DRAWING SHALL BE '4A'
3 | Callout | 1 | Francis L | Clarify whether there is any instrumentation shown as dotted.
4 | Call-out | 1 | Edgardo | The connection of this line in PID 050-A-PID-00008-2 is already shown as hatched / decommisioned; If it will also be decommisioned, this line should also be hatched
5 | Call-out | 1 | Edgardo | Please consider 1 1/2" drain valve to allow for faster draining time and connection of hoses