## 050-A-PID-50003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | Clarify function of HH
2 | Callout | 1 | Francis L | Indicate connections from PI-1709 and PI-1710 as per pump auto stop configuration on sht 12 of BMPS-A-50003. Applies to all similar pump controls.
3 | Callout | 1 | Mahdi Ali | SEQUENCE NUMBER FOR EQUIPMENT SHALL HAVE 4 DIGITS.
4 | Text Box | 1 | Francis L | Consider providing local field indicators readable from relevant bypass valves, if required.
5 | Callout | 1 | Francis L | Clarify function of LL and indicate in Note if required.
6 | Callout | 1 | A Albalooshi | Please confirm the design flow
7 | Callout | 1 | Abdul Rahim | Is this correct.Pls explain
8 | Callout | 1 | Francis L | Indicate as SP and close to relevant signal.
9 | Typewritten Text | 1 | Nabeel | Add 050P3278
10 | Typewritten Text | 1 | Nabeel | correct the direction of flow
11 | Typewritten Text | 1 | Nabeel | Define this line!
12 | Callout | 1 | Francis L | Clarify whether two separate signals (RVP and TVP) are required as outputs from the analyser.
13 | Callout | 1 | Abdul Rahim | Since flushing flow rate is small and intermittent. how these pumps are protected.
14 | Callout | 1 | Francis L | Value?
15 | Callout | 1 | A Albalooshi | Please provide 1 1/2" valve
16 | Text Box | 1 | Abdul Rahim | Explain from this configuration how LSR and MSR are transferred to Sitra separately