## 050-A-PID-50008-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Abdul Rahim | For Tanks 101,102 make suction MFD near these tank and route one line from these tank suction MFD to pumps 5034 A/B
2 | Callout | 1 | Abdul Rahim | Provide vent
3 | Callout | 1 | Abdul Rahim | Provide 1 1/2" drain
4 | Callout | 1 | Abdul Rahim | Provide flange with spacers for blinds
5 | Callout | 1 | Abdul Rahim | via P5034A/B
6 | Callout | 1 | Francis L | Connect directly to SEQ block of pump. Refer to auto stop configuration of pump on sht 12 of BMPS-A-50003.
7 | Call-out | 1 | Edgardo | Please clarify the requirement for this control valve. This line is supposed to be a rundown line to Sitra Tank Farm.
8 | Callout | 1 | Francis L | Indicate connections from these valves to the SEQ blocks above.
9 | Text Box | 1 | Francis L | Provide tag sequential numbers.