## 050-A-PID-50010-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | Rephrase to - TO 050P5061 A/B SEQ control
2 | Text Box | 1 | A Albalooshi | Tie in connections to tank 050D0503 is not shown please confirm
3 | Text Box | 1 | AliRedha Malalla | Please use Correct symbol for RV (vacuum), BMPS-A-50003
4 | Callout | 1 | Abdul Rahim | How many R/Vs
5 | Callout | 1 | Francis L | Rephrase to - FROM LI-0215
6 | Callout | 1 | Francis L | Amend to perforated stilling well
7 | Callout | 1 | Francis L | Clarify function and indicate against tag.
8 | Callout | 1 | Francis L | Improve clarity.
9 | Call-out | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Fan/Mixer/Cooler where possible. Motor FinFan tag nos. shall always be shown where applicable.
10 | Text Box | 1 | Francis L | Provide tag sequential numbers.
11 | Text Box | 1 | MAK | 050M5088
12 | Callout | 1 | Francis L | Indicate location for readability.
13 | Callout | 1 | Abdul Rahim | why this is bi directional
14 | Callout | 1 | Francis L | Amend to OVERRIDE
15 | Callout | 1 | Francis L | Indicate 4 digits
16 | Callout | 1 | Francis L | Remove LAL as it is repeated on LI-1752.
17 | Callout | 1 | Francis L | FIT
18 | Callout | 1 | A Albalooshi | Please confirm tank capacity & dimensions
19 | Callout | 1 | Mahdi Ali | REMOVE SPACE BETWEEN TAG NUMBER AND SUFFIX
20 | Callout | 1 | Francis L | Clarify whether this is a common fault alarm. and indicate against tag.
21 | Callout | 1 | Francis L | As per comments on pump A
22 | Callout | 1 | Francis L | Clarify whether a local indicator is required to be located at grade level.
23 | Callout | 1 | Francis L | Indicate arrow