## 050-A-PID-50011-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | as discussed T&I for tank should not be link to units T&I
2 | Callout | 1 | Abdul Rahim | This is N2 blanketed. Why this valve is required. never seen a normal valve for tank vent. pls discuss
3 | Callout | 1 | Abdul Rahim | from secondary header
4 | Callout | 1 | Francis L | Correct spelling
5 | Text Box | 1 | Abdul Rahim | During site survey check all existing roof manholes.
6 | Callout | 1 | Francis L | Indicate correct signal type (analog). Applies to other relevant loops.
7 | Callout | 1 | Abdul Rahim | how these will be installed on tank roof with propeeer support
8 | Callout | 1 | Abdul Rahim | The condition of existing are not good.
9 | Text Box | 1 | Edgardo | Please confirm the requirement for gooseneck vents on the tanks, which are nitrogen blanketed. The availability of vents, breather valves, and roof nozzles shall be verifed during the site survey; this comment applies to all tanks where new goosenek vents are proposed to be provided
10 | Callout | 1 | Abdul Rahim | from main header
11 | Text Box | 1 | AliRedha Malalla | Typical to all: Please use Correct symbol for RV (vacuum), BMPS-A-50003
12 | Text Box | 1 | Mahdi Ali | INCONSISTENT LINE THICKNESSES
13 | Callout | 1 | Abdul Rahim | Since PCVs are going to be installed on tank roof, pls ensure all necessary pressure and flow to be on repeated on the DCS
14 | Call-out | 1 | MAK | Change to: 050D0142
15 | Callout | 1 | Abdul Rahim | This is nothing to do with planning.
16 | Callout | 1 | Francis L | Clarify requirement of local indication and location. Applies to other similar applications.