## 050-A-PID-55002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | 050-A-PID-00001-01 | It will be updated to corresponding P&ID in next issue. | Y
2 | Call-out | 1 | Ahmed Marhoon | Add a note to describe the SEQ. | It will be included the sequence for MOVs description | Y
3 | Callout | 1 | Abdul Rahim | all comments on sheet 1 applies for sheet 2 | It will be included those comments that applies. | Y
4 | Typewritten Text | 1 | Nabeel | Change to "050D1002" | Noted. | Y
5 | Typewritten Text | 1 | Nabeel | Change to "050D1002" | Noted. | Y
6 | Typewritten Text | 1 | Nabeel | Change to "050P5033A/B/C" | It will be updated to final tagging in next revision. | N
7 | Call-out | 1 | Ahmed Ali | Drain to be moved as close as possible to the MOV to facilitate the draining of 20 inch line | It will be included at the low point of the line. | Y
8 | Callout | 1 | alexis.martinez | Each propeller mixer shall be shown separated and the the associated instrumentation as well. | Noted. | Y
9 | Typewritten Text | 1 | Nabeel | Follow Bapco numbering change to "050MX0013A/B" | It will be included according to equipment list final numbering. | N
10 | Call-out | 1 | A.Jabbar Mahmood | Further clarify note 3 (what is meant by Working Volume?) | Volume between HLL and LLL. | Y
11 | Call-out | 1 | Ahmed Marhoon | General for LA: add a note describing the common alarm for low low and high high level | It will be included a note next to LA | Y
12 | Callout | 1 | alexis.martinez | GENERAL: As per BMPS-A8, the streams leaving or enter the P&ID shall Include the name of the equipment and the complete tag number. Also the unit number abbreviated name when it is from/to other unit. | Noted. | Y
13 | Call-out | 1 | Edgardo | Please change size of drain to 1 1/2" to facilitate ease of draining when it is required to empty the line | Drain size will be increased to 1-1/2". | Y
14 | Call-out | 1 | Edgardo | Please confirm the appropriate location of the suction nozzle - either at shell or at bottom. | Connection is in shell as shown. | N/A
15 | Text Box | 1 | Ali Abbas | Refer to general comments in PID 55001 | Refer to reply of comment ID 3 | Y
16 | Call-out | 1 | Ahmed Marhoon | Review requirements for low and high level alarm for operator action. To be confirmed during Hazop3 | It will be review in HAZOP 3 | N
17 | Cloud+ | 1 | Ahmed Marhoon | Review the configuration of the mixer control and monitoring representation and correct the type of connections and functions. Refer to the typicals on symbology sheet and the configuration provided for the 1RHCU tank mixer on sheet 55003-001. Soft/Hard signals to be corrected, source/destination of signal to/from SEQ and Auto stop representation. Also applicable for 050MX5013 A/B. | It will be revised according to typical motors according to Symbology for each motor | Y
18 | Call-out | 1 | Edgardo | Show the B/L; this line is connected to unit 010 | To be defined once finalized unit numbering for pumping station. | N
19 | Call-out | 1 | Abdulaziz | Tank mixer shall be provided with clear maintenance access for removal and installation | Accesibility is accounted for and it will be included in 3D Model. | N/A
20 | Call-out | 1 | Ahmed Marhoon | Unlike the MOV at the tank's outlet, different serial numbers are assigned for the MOV-1002 and its accessories. Standardize wherever possible. Contractor to clarify. | It will be implemented. | Y
21 | Typewritten Text | 1 | Nabeel | We should have a Thermal Relief valve on the line between to valves | It is not required due to operating philosophy of this tank. | N