## 050-A-PID-55003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | 050-A-PID-00001-01
2 | Callout | 1 | Yousif Ahmadi | 4A
3 | Call-out | 1 | Ahmed Marhoon | According to the GAD issued for the 1RHCU tanks, there is an additional stilling well for independent direct level measurement. A note has been captured on the GAD to rectify the inconsistency between the documents. According to the mixer sequence, the GAD seems to be correct where the additional LIT will be used to stop the mixer/s and generate an alarm to the operator. Contractor to check and confirm.
4 | Callout | 1 | alexis.martinez | As per document 050-D-GAD-55003-001 additional level transmitter to be added.
5 | Call-out | 1 | Ahmed Marhoon | Change PIC to PC.
6 | Callout | 1 | Abdul Rahim | change to US barrles
7 | Cloud+ | 1 | Ahmed Marhoon | Compensation soft signal to be branched from the soft signal between TI and PI to FI. For 110# in symbology sheet for battery limit, flow is compensated by both temperature and pressure.
8 | Callout | 1 | Abdul Rahim | confirm requirement for check valve
9 | Call-out | 1 | Ahmed Marhoon | Contractor to clarify the purpose of the PHC. For a direct pressure control, PC is sufficient. 2 PHCs are required in case a split range loop is provided for the standard blanketing configuration i.e. with two control valves. Blanketing arrangement to be reviewed and confirmed taking into account different modes of operation in the tank and vapor space i.e. variation in tank's level. RV should be the last line of defense.
10 | Callout | 1 | Abdul Rahim | detailed tank internal and external is to be provided
11 | Call-out | 1 | A.Jabbar Mahmood | During EPC, a detailed steam distribution P&ID drawing shall be developed showing all branches on the distribution header.
12 | Callout | 1 | alexis.martinez | Each propeller mixer shall be shown separated and the the associated instrumentation as well.
13 | Callout | 1 | alexis.martinez | GENERAL: As per BMPS-A8, the streams leaving or enter the P&ID shall Include the name of the equipment and the complete tag number. Also the unit number abbreviated name when it is from/to other unit.
14 | Cloud+ | 1 | Ahmed Marhoon | Improve representation of FV/FY bubbles and the connected line to the component. Do not leave gaps. Typical for all control valves.
15 | Callout | 1 | Abdul Rahim | indicate size
16 | Callout | 1 | Abdul Rahim | is this control valve covers low range and high range or two control valves are required
17 | Call-out | 1 | Ahmed Marhoon | Note 11 is not applicable for the common LA.
18 | Callout | 1 | alexis.martinez | On the tank 050D1003 data block, the units in brackets for Diameter and Height shall be "mm" as per BMPS-A8
19 | Call-out | 1 | Edgardo | Please confirm this drawing number; Note that the format of this drawing number is not consistent with the standard format
20 | Call-out | 1 | Edgardo | Please confirm; Unit 000 is now replaced with Unit 930
21 | Callout | 1 | Abdul Rahim | provide vent
22 | Callout | 1 | Abdul Rahim | pump number not consistant with unit 050 BOD
23 | Call-out | 1 | Ali Abbas | Refer to general comments in PID 55001
24 | Typewritten Text | 1 | Nabeel | Replace with "050D1003"
25 | Cloud+ | 1 | Ahmed Marhoon | Requirement of alarms on TC-1718 to be confirmed during Hazop. However, in case alarms are required and associated with an operator action; they need to be generated by an independent temperature element. To avoid double failures (control and alarm) TE-1718 to be change to dual type where TE-1718A to be used for the control part and the new TE-1718B to be used for the alarms on DCS.
26 | Call-out | 1 | Edgardo | Show B/L; line is connected to Unit 018
27 | Callout | 1 | Abdul Rahim | steam lines and condensate to be insulated
28 | Cloud+ | 1 | Ahmed Marhoon | Steam tracing is to be provided up to the manifold and hence the steam tracing to be extended to the FIT bubble (only the vertical line)
29 | Cloud+ | 1 | Ahmed Marhoon | Steam tracing is to be provided up to the manifold and hence the steam tracing to be extended to the FIT bubble (only the vertical line)
30 | Callout | 1 | alexis.martinez | Tank blanketing system is inconsistent with FEED P&ID. The vent valve for out breathing and the associated instrumentation is missing. Review and do the corrections accordingly.
31 | Callout | 1 | Abdul Rahim | tank minmum level should always cover steam coils
32 | Call-out | 1 | Abdulaziz | Tank mixer shall be provided with clear maintenance access for removal and installation
33 | Callout | 1 | Abdul Rahim | this is not clear. is the spare installed on the tank. if two are installed one vacuum relief should be adequate for tank safety
34 | Callout | 1 | Abdul Rahim | this is preferred to be at ground level
35 | Callout | 1 | Abdul Rahim | this not as per BOD
36 | Callout | 1 | Abdul Rahim | tis should be working capacity
37 | Call-out | 1 | A.Jabbar Mahmood | TR to ensure that the pressure control scheme shall also take care of the high pressure senarios i.e. when the pressure exceeds the set point. Typical for the second tank
38 | Cloud+ | 1 | A.Jabbar Mahmood | TR to review and evaluate the requirement of an MOV acting as an EIV. Typical for the second tank
39 | Call-out | 1 | Ahmed Marhoon | Type of signal between temperature element and transmitter (050-T-1718) to be corrected.