## 050-A-PID-55004-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | all comments on D1003 applies for D1004 | All applicable comments will be included. | Y
2 | Callout | 1 | alexis.martinez | As per document 050-D-GAD-55004-001 additional level transmitter to be added. | Noted. | Y
3 | Callout | 1 | alexis.martinez | Each propeller mixer shall be shown separated and the the associated instrumentation as well. | Noted. | Y
4 | Callout | 1 | alexis.martinez | GENERAL: As per BMPS-A8, the streams leaving or enter the P&ID shall Include the name of the equipment and the complete tag number. Also the unit number abbreviated name when it is from/to other unit. | Noted. | Y
5 | Callout | 1 | alexis.martinez | On the tank 050D1004 data block, shall be barrels "bbl" for Capacity, as per BMPS-A8 | It will be updated accordingly | Y
6 | Callout | 1 | alexis.martinez | On the tank 050D1004 data block, the units in brackets for Diameter and Height shall be "mm" as per BMPS-A8 | It will be updated accordingly | Y
7 | Call-out | 1 | Ahmed Ali | please clarify the purpose and the source of the flushing oil? is it diesel? from where? | Currently there is no flushing facility, it will be provided flushing fcility through flushing oil of 3HDU pump | Y
8 | Call-out | 1 | Edgardo | Please indicate B/L; line is connected to unit 018 | It will be updated according to final resolution between tank and pumping station numbering | N
9 | Text Box | 1 | Ahmed Marhoon | Refer to comments on sheet 050-A-PID-55004-001 | Refer to reply in comment ID 1 | Y
10 | Call-out | 1 | Ali Abbas | Refer to general comments in PID 55001 | Refer to reply in comment ID 1 | Y
11 | Callout | 1 | alexis.martinez | Tank blanketing system is inconsistent with FEED P&ID. The vent valve for out breathing and the associated instrumentation is missing. Review and do the corrections accordingly. | Tank blanketing is according to HAZOP 2 and COMPANY recomendation, which requires to standarize all the blanketing systems for each tank of BMP. | N
12 | Call-out | 1 | Abdulaziz | Tank mixer shall be provided with clear maintenance access for removal and installation | Accesibility is accounted for and it will be included in 3D Model. | N/A