## 050-A-PID-55004-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | all comments on D1003 applies for D1004
2 | Callout | 1 | alexis.martinez | As per document 050-D-GAD-55004-001 additional level transmitter to be added.
3 | Callout | 1 | alexis.martinez | Each propeller mixer shall be shown separated and the the associated instrumentation as well.
4 | Callout | 1 | alexis.martinez | GENERAL: As per BMPS-A8, the streams leaving or enter the P&ID shall Include the name of the equipment and the complete tag number. Also the unit number abbreviated name when it is from/to other unit.
5 | Callout | 1 | alexis.martinez | On the tank 050D1004 data block, shall be barrels "bbl" for Capacity, as per BMPS-A8
6 | Callout | 1 | alexis.martinez | On the tank 050D1004 data block, the units in brackets for Diameter and Height shall be "mm" as per BMPS-A8
7 | Call-out | 1 | Ahmed Ali | please clarify the purpose and the source of the flushing oil? is it diesel? from where?
8 | Call-out | 1 | Edgardo | Please indicate B/L; line is connected to unit 018
9 | Text Box | 1 | Ahmed Marhoon | Refer to comments on sheet 050-A-PID-55004-001
10 | Call-out | 1 | Ali Abbas | Refer to general comments in PID 55001
11 | Callout | 1 | alexis.martinez | Tank blanketing system is inconsistent with FEED P&ID. The vent valve for out breathing and the associated instrumentation is missing. Review and do the corrections accordingly.
12 | Call-out | 1 | Abdulaziz | Tank mixer shall be provided with clear maintenance access for removal and installation