## 050-A-PID-55005-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Khalid | Connecting line missing | Drawing mistake, it will be updated in next issue. | Y
2 | Cloud+ | 1 | Ahmed Marhoon | Expansion to 4 inch is only required if the main line size is below 4 inch. For this case, the main line size is 4 inch and hence the expander/reducer arrangement is not required. | Reducers will be deleted. | Y
3 | Text Box | 1 | Ahmed Ali | General: as in all other process units, 60#, 110# and 60# steam headers are provided with double isolation valves and unit limit and by warm up 1.5" by pass on the second isolation valve. Please refer to 2HCU, 7CDU unit limit and apply the same. | It will be reissued once confirmed final configuration of units tanks and pumping station | Y
4 | Call-out | 1 | Ahmed Marhoon | Note 14 is not applicable on TE-1771. Should it be note 1? | Noted. | Y
5 | Call-out | 1 | Edgardo | Please confirm requirement for B/L; note that these lines are connected to different Units | It will be updated according to final resolution between tank and pumping station numbering | Y
6 | Callout | 1 | Abdul Rahim | this has nothing to do with Refinery Tanks unit 050. Change title | It will be updated according to final resolution between tank and pumping station numbering | Y
7 | Call-out | 1 | A.Jabbar Mahmood | This header feeds 3HDU and 2HCU and there are no connection to U50. It is not understood why this header is shown within U50, as part of TR's scope!. Check and confirm | It will be updated according to final resolution between tank and pumping station numbering | Y
8 | Call-out | 1 | A.Jabbar Mahmood | This header feeds 3HDU and 2HCU and there are no connection to U50. It is not understood why this header is shown within U50, as part of TR's scope!. Check and confirm | It will be updated according to final resolution between tank and pumping station numbering | Y
9 | Call-out | 1 | A.Jabbar Mahmood | This header originates from 3HDU and 2HCU and there are no connection to U50. It is not understood why this header is shown within U50, as part of TR's scope!. Check and confirm | It will be updated according to final resolution between tank and pumping station numbering | Y
10 | Call-out | 1 | A.Jabbar Mahmood | This header originates from 3HDU and 2HCU and there are no connection to U50. It is not understood why this header is shown within U50, as part of TR's scope!. Check and confirm | It will be updated according to final resolution between tank and pumping station numbering | Y
11 | Call-out | 1 | A.Jabbar Mahmood | This header originates from 3HDU and 2HCU and there are no connection to U50. It is not understood why this header is shown within U50, as part of TR's scope!. Check and confirm | It will be updated according to final resolution between tank and pumping station numbering | Y
12 | Text Box | 1 | Ahmed Ali | This is a condensate from 2HCU and some other units going to the refinery interconnection system, why is it showing in RTF? | It will be updated according to final resolution between tank and pumping station numbering | Y
13 | Text Box | 1 | alexis.martinez | This P&ID is not related with 1RHCU Feed Tanks or A/B Crude Oil Tanks. | It will be updated according to final resolution between tank and pumping station numbering | Y
14 | Call-out | 1 | Ahmed Ali | why globe valve? | Is a gate valve, drawing mistake, it will be updated in next issue. | Y