## 050-A-PID-55010-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | Delete
2 | Text Box | 1 | Ahmed.Marhoon | General: all DCS indications requested to be repeated on process units DCS respective graphics shall be provided with a note to indicate this requirement.
3 | Call-out | 1 | Ahmed.Marhoon | General: as a standard format, full description of the location to be reflected on the P&ID and not as a note.
4 | Call-out | 1 | Ahmed.Marhoon | General: local indicators to be shown on the P&IDs. Those local indicators to be readable from the respective equipment such as bypass valves.
5 | Callout | 1 | alexis.martinez | GENERAL: Review the need of fisical flange to indicate Operating Center Battery Limit. Include more flanges that are not really required is add more leak points in the system.
6 | Call-out | 1 | Ahmed.Marhoon | General: Contractor to critically review the diaphragm seals provided on the DP type flow meters as they will impact accuracy. Normally, no diaphragm seals are provided on FITs. Contractor to review and confirm.
7 | Text Box | 1 | Mahdi Ali | 1. TAG NUMBER FOR THE DRIVER FOR ROTATING EQUIPMENT SUCH AS PUMPS OR COMPRESSORS SHALL BE INSERTED ON ALL PIDS AS PER BMPS-A8 SECTION 8.4.3. 2. USE UPDATED LINE TYPE FOR FIELDBUS SIGNAL. 3. MAKE SURE THAT CORRECT OPC TYPE IS USED FOR UTILITIES AND PROCESS 4. TTSJV SHALL REQUEST A BLOCK OF LINE NUMBERS FROM BAPCO TO USE FOR THE REVAMP AREAS.