## 050-A-PID-55012-002-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Sameer Foujdar | General Comment: All buried lines (Bu) are shown as full lines as per the revised BMPS 50003
2 | Call-out | 1 | Ahmed.Marhoon | General: All instruments in PITs to be safely accessible from grade.
3 | Cloud+ | 1 | MAK | Delete
4 | Call-out | 1 | Sameer Foujdar | Review the comment is compete.
5 | Call-out | 1 | Sameer Foujdar | Check and confirm the line numbers for the Cooling water supply and return headers it should be in line with Unit 930 PID sheet no 8.
6 | Callout | 1 | alexis.martinez | Show the break of Buried and Above Ground line as per BMPS-A-50003
7 | Call-out | 1 | Ahmed.Marhoon | General: Analyzers details to be shown on P&ID (sample return, isolations ...etc). Also ensure that the analyzer is installed in appropriate location (house, shelter .... etc)