## 050-D-GAD-55001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | requiremnt for at least two free manways
2 | Cloud+ | 1 | Mohamed Ayyash | General Comment : Move Unit title back to center of cell. Apply to all GAD drawings.
3 | Callout | 1 | Yousif Ahmadi | 100% per FEED datasheet
4 | Call-out | 1 | Edgardo | Please refer to Clause 5.7.6.1 of BMPS-D2 regarding requirements for sizes of manway
5 | Text Box | 1 | Mahdi Ali | Change the orientation of the drawings.
6 | Call-out | 1 | MAK | Change to 050D1001. All tag nos. shall be as per the agreed and final equipment lists.
7 | Text Box | 1 | MAK | General Comment: Texts font style and size shall not be changed. Every drawing border is predefined with font style and size.
8 | Callout | 1 | Abdul Rahim | what is the basis of these figure?
9 | Callout | 1 | Erwin.Lugue | Units shall be in S.I.
10 | Callout | 1 | Abdul Rahim | tank working capacity should be 200000 bbls
11 | Callout | 1 | Abdul Rahim | to be suitable for crude service
12 | Call-out | 1 | Edgardo | This drawing title does not reflect the contents of all the pages for this drawing number. As an example, Sheet 3 is showing the elevation view
13 | Text Box | 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
14 | Callout | 1 | Abdul Rahim | wind girder is required
15 | Callout | 1 | Erwin.Lugue | To include load values in metric units
16 | Callout | 1 | Abdul Rahim | this is required for foam pourer
17 | Callout | 1 | Abdul Rahim | check this not correct
18 | Callout | 1 | Abdul Rahim | confirm requirement
19 | Text Box | 1 | Ahmed Marhoon | Size of nozzles for the temperature gauges to be verified/confirmed by contractor with respect to BMPS-J2 and BMPS typical drawings (4 inch Vs 1.5 inc).
20 | Call-out | 1 | Ahmed Marhoon | Comments on GAD-55001-001, 002, 003 and 004 of tank 050D0001 are also applicable for GADs of tank 050D0002.
21 | Callout | 1 | Erwin.Lugue | To include load values in metric units. Calculation of the wind loads shall be as per the approved code in the basis of design
22 | Callout | 1 | Abdul Rahim | indicate who is OTHERS ?
23 | Callout | 1 | Abdul Rahim | This tag is different that Basis of design 050D1001
24 | Call-out | 1 | Ahmed Marhoon | Details of the level and temperature instruments nozzles (including stilling well) to be updated based on the latest standard drawing. Refer to comment on note 19 on sheet 2 of this GAD.