## 050-D-GAD-55001-002-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | All text shall be in UPPERCASE
2 | Call-out | 1 | Ahmed Marhoon | Note 19: Latest standard stilling well and thermowell detail drawing for the floating roof tanks to be referenced and followed in the design. Owner's drawing can be requested/provided at the JVD for the necessary distribution to all OCs.
3 | Text Box | 1 | Ahmed Ali | General: for all pages there is no title, service or equipment number for this document
4 | Callout | 1 | Yousif Ahmadi | 3/8" = 9.6 mm
5 | Callout | 1 | Abdul Rahim | change to galoon per minute
6 | Call-out | 1 | Ahmed Marhoon | Note 15: Instrumentation nozzles to be finalized post detail design development and Hazop3/SIL sessions taking into account the process operating requirements. Note to be amended accordingly.
7 | Callout | 1 | Abdul Rahim | explain item 28. auto bleeder (vacuum breaker) this is clear. rim vent and gauge hatch is not clear for this item. may be need to split.
8 | Callout | 1 | Abdul Rahim | each pontoon manway to be provided with goose neck type pipe for gas test
9 | Callout | 1 | Yousif Ahmadi | remove the word "two"
10 | Callout | 1 | Abdul Rahim | rim vent to be confirmd
11 | Callout | 1 | Abdul Rahim | D1001 and 1002
12 | Callout | 1 | Abdul Rahim | pontoon manway to be provided with goose neck type pipe for gas test