## 050-D-GAD-55001-003-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Erwin.Lugue | Missing Draw-off sump & inspection wells
2 | Callout | 1 | Robert.Kawitzki | Reference Drg No for notes?
3 | Typewritten Text | 1 | Nabeel | Two Stilling well are required, one for the Radar Gauge and the other for Manual Gauging. Show the Datum Plate.
4 | Callout | 1 | Erwin.Lugue | Self-anchored ? Provide anchoring details
5 | Callout | 1 | Abdul Rahim | detail of piping to be approved by owner
6 | Call-out | 1 | Edgardo | Although the elevation of this suction nozzle is shown as HOLD, please ensure that the elevation of the suction nozzle will meet the required minimum tank level and its upturn nozzle will not hit the roof when at low leg position
7 | Typewritten Text | 1 | Nabeel | Earthing should be provided
8 | Call-out | 1 | Edgardo | Instead of mechanical seal, the roof seal is appropriately called the primary roof seal and the secondary roof seal
9 | Typewritten Text | 1 | Nabeel | A side valve should be added, it is used during the annual testing of the foam pourer
10 | Typewritten Text | 1 | Nabeel | None Return Valve to be mentioned at the Jack Knife Drain
11 | Callout | 1 | Abdul Rahim | manway size to be larger than mixer blades
12 | Call-out | 1 | Ahmed Marhoon | Nozzle 5CN is for temperature measurement and hence the "holed" stilling well is not applicable. Refer to the latest standard drawing for details of the thermowell pipe requirement.
13 | Typewritten Text | 1 | Nabeel | Holes in wind girder for water draining purposes
14 | Callout | 1 | Abdul Rahim | clearly identify no. of free manways,
15 | Callout | 1 | Abdul Rahim | consider suction nozzle to be in tank bottom with up turn elbow to prevent free water routed in unit feed line suction
16 | Call-out | 1 | 986131 | Show Working level Normal Fill level and minimum fill level
17 | Callout | 1 | Abdul Rahim | foam pourer nozle to be provided with birds nest mesh
18 | Callout | 1 | Abdul Rahim | two independant stilling is required one for radar gauge and one for custody manual gauging
19 | Callout | 1 | Abdul Rahim | roof drain type tp be approved by owner
20 | Callout | 1 | Erwin.Lugue | Stair layout has to be provided and details in accordance with BMPS-D2 & BMPS-A5
21 | Callout | 1 | Robert.Kawitzki | And BMPS-A4
22 | Callout | 1 | Robert.Kawitzki | Complete Drawing form
23 | Callout | 1 | Abdul Rahim | rolling ladder track design to be approved by owner
24 | Call-out | 1 | Edgardo | As shown below, the foam piping is blocking access on the windgirder. This is not acceptable as access through the windgirder is required
25 | Callout | 1 | Abdul Rahim | explain the purpose
26 | Callout | 1 | Abdul Rahim | foam dam plate should be below top tank shell at max operating height
27 | Callout | 1 | Erwin.Lugue | Missing Roof & Platform
28 | Typewritten Text | 1 | Nabeel | What is the height of the hand rail? should meet Bapco requirement
29 | Call-out | 1 | Ahmed Marhoon | Number of stilling wells/nozzle shall be finalized based on the final P&ID, Hazop/SIL studies and selected type of level transmitter. Currently, only 9N is shown as a common stilling well for three purposes (per the P&ID) which is incorrect.
30 | Callout | 1 | Abdul Rahim | earthing boss is required for lighting from tank top
31 | Typewritten Text | 1 | Nabeel | NO Mentioning about the shunts used for the tank protection against lighting