## 050-D-GAD-55003-002-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | steam coils to be covered by liquid at all time. ie min operating level should cover the steam coils
2 | Callout | 1 | Abdul Rahim | it is assume a multi level transmitter will be used
3 | Call-out | 1 | Ahmed Marhoon | Note 22: Latest standard stilling well and thermowell detail drawing for the Dome roof tanks to be referenced and followed in the design. Owner's drawing can be requested/provided at the JVD for the necessary distribution to all OCs.
4 | Call-out | 1 | Ahmed Marhoon | Note 37: Instrumentation nozzles to be finalized post detail design development and Hazop3/SIL sessions taking into account the process operating requirements. Note to be amended accordingly.