## 050-D-GAD-55003-003-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | will there be a diffuser inside the tank
2 | Callout | 1 | Abdul Rahim | according to unit 050 BOD tag is 050D1003
3 | Call-out | 1 | 986131 | Show Working level Normal Fill level and minimum fill level
4 | Callout | 1 | Abdul Rahim | explain the use of pressure transmitter
5 | Call-out | 1 | Ahmed Marhoon | Number & details of stilling wells is not covered in the Nozzle Schedule. Also, number of stilling wells/nozzles shall be finalized based on the final P&ID, Hazop/SIL studies and selected type of level transmitter.
6 | Callout | 1 | Erwin.Lugue | Stair layout has to be provided and details in accordance with BMPS-D2 & BMPS-A5
7 | Callout | 1 | Abdul Rahim | Manway size to be larger than mixer bladdes
8 | Call-out | 1 | Ahmed Marhoon | Nozzle 2CN is for temperature measurement and hence the "holed" stilling well is not applicable. Refer to the latest standard drawing for details of the thermowell pipe requirement.
9 | Callout | 1 | Abdul Rahim | All sample lines to be installed inside the tank, all sample lines to be routed out of the tank in a sample tandish out side the tank at approx 1 M height. ask for check Bapco standard drawing
10 | Callout | 1 | Abdul Rahim | confirm how many level transmitters
11 | Call-out | 1 | Ahmed Marhoon | Review the requirement for manual gauging stilling well.
12 | Callout | 1 | Abdul Rahim | details for support to be shown
13 | Callout | 1 | Erwin.Lugue | Missing Draw-off sump & inspection wells